## units
CaseStudy | Reference | Scenario | Unit | Type | UnitName | ToUnitName | FromPort | Parameter
SEAWATER
ashkelon | nawi | baseline | sw_onshore_intake | intake | sw_onshore_intake | sulfuric_acid_addition | outlet | {'water_type': ['seawater']}
ashkelon | nawi | baseline | sulfuric_acid_addition | treatment | sulfuric_acid_addition | ferric_chloride_addition | outlet | {'dose': 10}
ashkelon | nawi | baseline | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'dose': 20}
ashkelon | nawi | baseline | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
ashkelon | nawi | baseline | static_mixer | treatment | static_mixer | tri_media_filtration | outlet
ashkelon | nawi | baseline | tri_media_filtration | treatment | tri_media_filtration | cartridge_filtration,backwash_solids_handling | outlet,waste
ashkelon | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration | ro_first_pass | outlet
ashkelon | nawi | baseline | reverse_osmosis | treatment | ro_first_pass | lime_softening,ro_first_stage | outlet,waste | {'erd': 'no'}
ashkelon | nawi | baseline | reverse_osmosis | treatment | ro_first_stage | lime_softening | outlet | {'erd': 'yes'}
ashkelon | nawi | baseline | lime_softening | treatment | lime_softening | chlorination_b | outlet | {'lime': 2.3}
ashkelon | nawi | baseline | chlorination | treatment | chlorination_b | caustic_soda_addition | outlet | {'chemical_name': 'Chlorine'}
ashkelon | nawi | baseline | caustic_soda_addition | treatment | caustic_soda_addition | treated_storage | outlet | {'dose': 30}
ashkelon | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 1}
ashkelon | nawi | baseline | backwash_solids_handling | treatment | backwash_solids_handling | landfill | waste | {'recovery': 0.95}
ashkelon | nawi | baseline | municipal_drinking | use | municipal_drinking
ashkelon | nawi | baseline | surface_discharge | waste | surface_discharge
ashkelon | nawi | baseline | landfill | waste | landfill
ashkelon | nawi | one_ro | sw_onshore_intake | intake | sw_onshore_intake | sulfuric_acid_addition | outlet | {'water_type': ['seawater']}
ashkelon | nawi | one_ro | sulfuric_acid_addition | treatment | sulfuric_acid_addition | ferric_chloride_addition | outlet | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 10}
ashkelon | nawi | one_ro | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 20}
ashkelon | nawi | one_ro | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
ashkelon | nawi | one_ro | static_mixer | treatment | static_mixer | tri_media_filtration | outlet
ashkelon | nawi | one_ro | tri_media_filtration | treatment | tri_media_filtration | cartridge_filtration,backwash_solids_handling | outlet,waste
ashkelon | nawi | one_ro | cartridge_filtration | treatment | cartridge_filtration | ro_first_pass | outlet
ashkelon | nawi | one_ro | reverse_osmosis | treatment | ro_first_pass | lime_softening | outlet | {'pump': 'yes', 'feed_pressure': 85, 'erd': 'yes'}
ashkelon | nawi | one_ro | lime_softening | treatment | lime_softening | chlorination_b | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
ashkelon | nawi | one_ro | chlorination | treatment | chlorination_b | caustic_soda_addition | outlet | {'chemical_name': 'Chlorine'}
ashkelon | nawi | one_ro | caustic_soda_addition | treatment | caustic_soda_addition | treated_storage | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
ashkelon | nawi | one_ro | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 1}
ashkelon | nawi | one_ro | backwash_solids_handling | treatment | backwash_solids_handling | landfill | waste | {'recovery': 0.95}
ashkelon | nawi | one_ro | municipal_drinking | use | municipal_drinking
ashkelon | nawi | one_ro | surface_discharge | waste | surface_discharge
ashkelon | nawi | one_ro | landfill | waste | landfill
carlsbad | nawi | baseline | sw_onshore_intake | intake | sw_onshore_intake | sulfuric_acid_addition | outlet | {'water_type': ['seawater']}
carlsbad | nawi | baseline | sulfuric_acid_addition | treatment | sulfuric_acid_addition | ferric_chloride_addition | outlet | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 10}
carlsbad | nawi | baseline | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 20}
carlsbad | nawi | baseline | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
carlsbad | nawi | baseline | static_mixer | treatment | static_mixer | tri_media_filtration | outlet
carlsbad | nawi | baseline | tri_media_filtration | treatment | tri_media_filtration | cartridge_filtration,backwash_solids_handling | outlet,waste
carlsbad | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration | ro_first_pass | outlet
carlsbad | nawi | baseline | reverse_osmosis | treatment | ro_first_pass | lime_softening,ro_first_stage | outlet,waste | {'pump': 'yes', 'feed_pressure': 85, 'erd': 'no'}
carlsbad | nawi | baseline | reverse_osmosis | treatment | ro_first_stage | lime_softening | outlet | {'pump': 'yes', 'feed_pressure': 85, 'erd': 'yes'}
carlsbad | nawi | baseline | lime_softening | treatment | lime_softening | chlorination_b | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
carlsbad | nawi | baseline | chlorination | treatment | chlorination_b | caustic_soda_addition | outlet | {'chemical_name': 'Chlorine'}
carlsbad | nawi | baseline | caustic_soda_addition | treatment | caustic_soda_addition | treated_storage | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
carlsbad | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 1}
carlsbad | nawi | baseline | backwash_solids_handling | treatment | backwash_solids_handling | landfill | waste | {'recovery': 0.95}
carlsbad | nawi | baseline | municipal_drinking | use | municipal_drinking
carlsbad | nawi | baseline | surface_discharge | waste | surface_discharge
carlsbad | nawi | baseline | landfill | waste | landfill
carlsbad | nawi | one_ro | sw_onshore_intake | intake | sw_onshore_intake | sulfuric_acid_addition | outlet | {'water_type': ['seawater']}
carlsbad | nawi | one_ro | sulfuric_acid_addition | treatment | sulfuric_acid_addition | ferric_chloride_addition | outlet | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 10}
carlsbad | nawi | one_ro | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 20}
carlsbad | nawi | one_ro | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
carlsbad | nawi | one_ro | static_mixer | treatment | static_mixer | tri_media_filtration | outlet
carlsbad | nawi | one_ro | tri_media_filtration | treatment | tri_media_filtration | cartridge_filtration,backwash_solids_handling | outlet,waste
carlsbad | nawi | one_ro | cartridge_filtration | treatment | cartridge_filtration | ro_first_pass | outlet
carlsbad | nawi | one_ro | reverse_osmosis | treatment | ro_first_pass | lime_softening | outlet | {'pump': 'yes', 'feed_pressure': 85, 'erd': 'yes'}
carlsbad | nawi | one_ro | lime_softening | treatment | lime_softening | chlorination_b | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
carlsbad | nawi | one_ro | chlorination | treatment | chlorination_b | caustic_soda_addition | outlet | {'chemical_name': 'Chlorine'}
carlsbad | nawi | one_ro | caustic_soda_addition | treatment | caustic_soda_addition | treated_storage | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
carlsbad | nawi | one_ro | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 1}
carlsbad | nawi | one_ro | backwash_solids_handling | treatment | backwash_solids_handling | landfill | waste | {'recovery': 0.95}
carlsbad | nawi | one_ro | municipal_drinking | use | municipal_drinking
carlsbad | nawi | one_ro | surface_discharge | waste | surface_discharge
carlsbad | nawi | one_ro | landfill | waste | landfill
santa_barbara | nawi | baseline | sw_onshore_intake | intake | sw_onshore_intake | ferric_chloride_addition | outlet | {'water_type': ['seawater']}
santa_barbara | nawi | baseline | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 20}
santa_barbara | nawi | baseline | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
santa_barbara | nawi | baseline | static_mixer | treatment | static_mixer | holding_tank | outlet
santa_barbara | nawi | baseline | treated_storage | treatment | holding_tank | media_filtration | outlet | {'hours': 2}
santa_barbara | nawi | baseline | basic_unit | treatment | media_filtration | anti_scalant_addition,backwash_solids_handling | outlet,waste | {'unit_process_name': 'media_filtration'}
santa_barbara | nawi | baseline | anti_scalant_addition | treatment | anti_scalant_addition | cartridge_filtration | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
santa_barbara | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration | reverse_osmosis | outlet
santa_barbara | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | holding_tank_b | outlet | {'pump': 'yes', 'feed_pressure': 85,'erd': 'yes'}
santa_barbara | nawi | baseline | treated_storage | treatment | holding_tank_b | uv_aop | outlet | {'hours': 1}
santa_barbara | nawi | baseline | uv_aop | treatment | uv_aop | co2_addition | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 350, 'aop': True, 'uvt_in': 0.95}
santa_barbara | nawi | baseline | co2_addition | treatment | co2_addition | lime_addition | outlet
santa_barbara | nawi | baseline | lime_addition | treatment | lime_addition | treated_storage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
santa_barbara | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 1}
santa_barbara | nawi | baseline | backwash_solids_handling | treatment | backwash_solids_handling | landfill,landfill | outlet,waste
santa_barbara | nawi | baseline | landfill | waste | landfill
santa_barbara | nawi | baseline | municipal_drinking | use | municipal_drinking
tampa_bay | nawi | one_ro | sw_onshore_intake | intake | sw_onshore_intake | sulfuric_acid_addition | outlet | {'water_type': ['seawater']}
tampa_bay | nawi | one_ro | sulfuric_acid_addition | treatment | sulfuric_acid_addition | ferric_chloride_addition | outlet | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 10}
tampa_bay | nawi | one_ro | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 20}
tampa_bay | nawi | one_ro | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
tampa_bay | nawi | one_ro | static_mixer | treatment | static_mixer | tri_media_filtration | outlet
tampa_bay | nawi | one_ro | tri_media_filtration | treatment | tri_media_filtration | cartridge_filtration,backwash_solids_handling | outlet,waste
tampa_bay | nawi | one_ro | cartridge_filtration | treatment | cartridge_filtration | ro_first_pass | outlet
tampa_bay | nawi | one_ro | reverse_osmosis | treatment | ro_first_pass | lime_softening | outlet | {'pump': 'yes', 'feed_pressure': 65, 'erd': 'yes'}
tampa_bay | nawi | one_ro | lime_softening | treatment | lime_softening | chlorination_b | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
tampa_bay | nawi | one_ro | chlorination | treatment | chlorination_b | caustic_soda_addition | outlet | {'chemical_name': 'Chlorine'}
tampa_bay | nawi | one_ro | caustic_soda_addition | treatment | caustic_soda_addition | ammonia_addition | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
tampa_bay | nawi | one_ro | ammonia_addition | treatment | ammonia_addition | treated_storage | outlet | {'chemical_name': ['Ammonia'], 'dose': 3}
tampa_bay | nawi | one_ro | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
tampa_bay | nawi | one_ro | backwash_solids_handling | treatment | backwash_solids_handling | landfill,landfill | outlet,waste | {'recovery': 0.95}
tampa_bay | nawi | one_ro | municipal_drinking | use | municipal_drinking
tampa_bay | nawi | one_ro | surface_discharge | waste | surface_discharge
tampa_bay | nawi | one_ro | landfill | waste | landfill
tampa_bay | nawi | baseline | sw_onshore_intake | intake | sw_onshore_intake | sulfuric_acid_addition | outlet | {'water_type': ['seawater']}
tampa_bay | nawi | baseline | sulfuric_acid_addition | treatment | sulfuric_acid_addition | ferric_chloride_addition | outlet | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 10}
tampa_bay | nawi | baseline | ferric_chloride_addition | treatment | ferric_chloride_addition | chlorination | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 20}
tampa_bay | nawi | baseline | chlorination | treatment | chlorination | static_mixer | outlet | {'chemical_name': 'Chlorine'}
tampa_bay | nawi | baseline | static_mixer | treatment | static_mixer | tri_media_filtration | outlet
tampa_bay | nawi | baseline | tri_media_filtration | treatment | tri_media_filtration | cartridge_filtration,backwash_solids_handling | outlet,waste
tampa_bay | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration | ro_first_pass | outlet
tampa_bay | nawi | baseline | reverse_osmosis | treatment | ro_first_pass | lime_softening,ro_second_pass | outlet,outlet | {'pump': 'yes', 'feed_pressure': 65, 'erd': 'yes', 'split_fraction': [0.67, 0.33]}
tampa_bay | nawi | baseline | reverse_osmosis | treatment | ro_second_pass | lime_softening | outlet | {'pump': 'yes', 'feed_pressure': 35, 'erd': 'yes'}
tampa_bay | nawi | baseline | lime_softening | treatment | lime_softening | chlorination_b | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
tampa_bay | nawi | baseline | chlorination | treatment | chlorination_b | caustic_soda_addition | outlet | {'chemical_name': 'Chlorine'}
tampa_bay | nawi | baseline | caustic_soda_addition | treatment | caustic_soda_addition | ammonia_addition | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
tampa_bay | nawi | baseline | ammonia_addition | treatment | ammonia_addition | treated_storage | outlet | {'chemical_name': ['Ammonia'], 'dose': 3}
tampa_bay | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
tampa_bay | nawi | baseline | backwash_solids_handling | treatment | backwash_solids_handling | landfill,landfill | outlet,waste | {'recovery': 0.95}
tampa_bay | nawi | baseline | municipal_drinking | use | municipal_drinking
tampa_bay | nawi | baseline | surface_discharge | waste | surface_discharge
tampa_bay | nawi | baseline | landfill | waste | landfill
BRACKISH
emwd | nawi | baseline | well_field | intake | well_field | iron_and_manganese_removal | outlet | {'water_type': ['emwd_ca_brackish']}
emwd | nawi | baseline | iron_and_manganese_removal | treatment | iron_and_manganese_removal | decarbonator_a,cartridge_filtration_a,chlorination,cartridge_filtration_b | outlet,outlet,outlet,outlet | {'split_fraction': [0.033, 0.467, 0.116, 0.384]}
emwd | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration_a | ro_a1,ro_a2 | outlet,outlet | {'split_fraction': [0.5, 0.5]}
emwd | nawi | baseline | reverse_osmosis | treatment | ro_a1 | decarbonator_a | outlet | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | baseline | reverse_osmosis | treatment | ro_a2 | decarbonator_a | outlet | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | baseline | basic_unit | treatment | decarbonator_a | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration_b | ro_b1,ro_b2 | outlet,outlet | {'split_fraction': [0.5, 0.5]}
emwd | nawi | baseline | reverse_osmosis | treatment | ro_b1 | decarbonator_b | outlet | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | baseline | reverse_osmosis | treatment | ro_b2 | decarbonator_b | outlet | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | baseline | basic_unit | treatment | decarbonator_b | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | baseline | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
emwd | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 3}
emwd | nawi | baseline | municipal_drinking | use | municipal_drinking
emwd | nawi | baseline | surface_discharge | waste | surface_discharge
(what-if: implemented deep well injection)
emwd | nawi | dwi | well_field | intake | well_field | iron_and_manganese_removal | outlet | {'water_type': ['emwd_ca_brackish']}
emwd | nawi | dwi | iron_and_manganese_removal | treatment | iron_and_manganese_removal | decarbonator_a,cartridge_filtration_a,chlorination,cartridge_filtration_b | outlet,outlet,outlet,outlet | {'split_fraction': [0.033, 0.467, 0.116, 0.384]}
emwd | nawi | dwi | cartridge_filtration | treatment | cartridge_filtration_a | ro_a1,ro_a2 | outlet,outlet | {'split_fraction': [0.5, 0.5]}
emwd | nawi | dwi | reverse_osmosis | treatment | ro_a1 | decarbonator_a,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | dwi | reverse_osmosis | treatment | ro_a2 | decarbonator_a,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | dwi | basic_unit | treatment | decarbonator_a | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | dwi | cartridge_filtration | treatment | cartridge_filtration_b | ro_b1,ro_b2 | outlet,outlet | {'split_fraction': [0.5, 0.5]}
emwd | nawi | dwi | reverse_osmosis | treatment | ro_b1 | decarbonator_b,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | dwi | reverse_osmosis | treatment | ro_b2 | decarbonator_b,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | dwi | basic_unit | treatment | decarbonator_b | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | dwi | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
emwd | nawi | dwi | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 3}
emwd | nawi | dwi | municipal_drinking | use | municipal_drinking
emwd | nawi | dwi | deep_well_injection | waste | deep_well_injection |  |  | {'pipe_distance': 10, 'lift_height': 400}
(what-if: ZLD-A: RO1 > Lime Softening > RO2 > Evaporation Pond + Landfill)
emwd | nawi | zld_a | well_field | intake | well_field | iron_and_manganese_removal | outlet | {'water_type': ['emwd_ca_brackish']}
emwd | nawi | zld_a | iron_and_manganese_removal | treatment | iron_and_manganese_removal | decarbonator_a,cartridge_filtration_a,chlorination,cartridge_filtration_b | outlet,outlet,outlet,outlet | {'split_fraction': [0.033, 0.467, 0.116, 0.384]}
emwd | nawi | zld_a | cartridge_filtration | treatment | cartridge_filtration_a | ro_a_first_pass | outlet
emwd | nawi | zld_a | reverse_osmosis | treatment | ro_a_first_pass | decarbonator_a,passthrough_a | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_a | basic_unit | treatment | passthrough_a | lime_softening_a | outlet | {'unit_process_name': 'passthrough'}
emwd | nawi | zld_a | lime_softening | treatment | lime_softening_a | ro_a_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 200}
emwd | nawi | zld_a | reverse_osmosis | treatment | ro_a_second_pass | decarbonator_a,evaporation_pond | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_a | basic_unit | treatment | decarbonator_a | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | zld_a | cartridge_filtration | treatment | cartridge_filtration_b | ro_b_first_pass | outlet
emwd | nawi | zld_a | reverse_osmosis | treatment | ro_b_first_pass | decarbonator_b,passthrough_b | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_a | basic_unit | treatment | passthrough_b | lime_softening_b | outlet | {'unit_process_name': 'passthrough'}
emwd | nawi | zld_a | lime_softening | treatment | lime_softening_b | ro_b_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 200}
emwd | nawi | zld_a | reverse_osmosis | treatment | ro_b_second_pass | decarbonator_b,evaporation_pond | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_a | basic_unit | treatment | decarbonator_b | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | zld_a | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
emwd | nawi | zld_a | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 3}
emwd | nawi | zld_a | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
emwd | nawi | zld_a | municipal_drinking | use | municipal_drinking
emwd | nawi | zld_a | landfill_zld | waste | landfill_zld
(what-if: ZLD-B: RO1 > Lime Softening > RO2 > Brine Concentrator > Evaporation Pond + Landfill)
emwd | nawi | zld_b | well_field | intake | well_field | iron_and_manganese_removal | outlet | {'water_type': ['emwd_ca_brackish']}
emwd | nawi | zld_b | iron_and_manganese_removal | treatment | iron_and_manganese_removal | decarbonator_a,cartridge_filtration_a,chlorination,cartridge_filtration_b | outlet,outlet,outlet,outlet | {'split_fraction': [0.033, 0.467, 0.116, 0.384]}
emwd | nawi | zld_b | cartridge_filtration | treatment | cartridge_filtration_a | ro_a_first_pass | outlet
emwd | nawi | zld_b | reverse_osmosis | treatment | ro_a_first_pass | decarbonator_a,passthrough_a | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_b | basic_unit | treatment | passthrough_a | lime_softening_a | outlet | {'unit_process_name': 'passthrough'}
emwd | nawi | zld_b | lime_softening | treatment | lime_softening_a | ro_a_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
emwd | nawi | zld_b | reverse_osmosis | treatment | ro_a_second_pass | decarbonator_a,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_b | basic_unit | treatment | decarbonator_a | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | zld_b | cartridge_filtration | treatment | cartridge_filtration_b | ro_b_first_pass | outlet
emwd | nawi | zld_b | reverse_osmosis | treatment | ro_b_first_pass | decarbonator_b,passthrough_b | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_b | basic_unit | treatment | passthrough_b | lime_softening_b | outlet | {'unit_process_name': 'passthrough'}
emwd | nawi | zld_b | lime_softening | treatment | lime_softening_b | ro_b_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
emwd | nawi | zld_b | reverse_osmosis | treatment | ro_b_second_pass | decarbonator_b,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_b | basic_unit | treatment | decarbonator_b | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | zld_b | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
emwd | nawi | zld_b | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 3}
emwd | nawi | zld_b | brine_concentrator | treatment | brine_concentrator | treated_storage,evaporation_pond | outlet,waste
emwd | nawi | zld_b | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
emwd | nawi | zld_b | municipal_drinking | use | municipal_drinking
emwd | nawi | zld_b | landfill_zld | waste | landfill_zld |  |  | {'pipe_distance': 0, 'lift_height': 400}
(what-if: ZLD-C: RO1 > Lime Softening > RO2 > Brine Concentrator > Crystallizer > Landfill)
emwd | nawi | zld_c | well_field | intake | well_field | iron_and_manganese_removal | outlet | {'water_type': ['emwd_ca_brackish']}
emwd | nawi | zld_c | iron_and_manganese_removal | treatment | iron_and_manganese_removal | decarbonator_a,cartridge_filtration_a,chlorination,cartridge_filtration_b | outlet,outlet,outlet,outlet | {'split_fraction': [0.033, 0.467, 0.116, 0.384]}
emwd | nawi | zld_c | cartridge_filtration | treatment | cartridge_filtration_a | ro_a_first_pass | outlet
emwd | nawi | zld_c | reverse_osmosis | treatment | ro_a_first_pass | decarbonator_a,passthrough_a | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_c | basic_unit | treatment | passthrough_a | lime_softening_a | outlet | {'unit_process_name': 'passthrough'}
emwd | nawi | zld_c | lime_softening | treatment | lime_softening_a | ro_a_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
emwd | nawi | zld_c | reverse_osmosis | treatment | ro_a_second_pass | decarbonator_a,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_c | basic_unit | treatment | decarbonator_a | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | zld_c | cartridge_filtration | treatment | cartridge_filtration_b | ro_b_first_pass | outlet
emwd | nawi | zld_c | reverse_osmosis | treatment | ro_b_first_pass | decarbonator_b,passthrough_b | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_c | basic_unit | treatment | passthrough_b | lime_softening_b | outlet | {'unit_process_name': 'passthrough'}
emwd | nawi | zld_c | lime_softening | treatment | lime_softening_b | ro_b_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
emwd | nawi | zld_c | reverse_osmosis | treatment | ro_b_second_pass | decarbonator_b,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
emwd | nawi | zld_c | basic_unit | treatment | decarbonator_b | chlorination | outlet | {'unit_process_name': 'decarbonator'}
emwd | nawi | zld_c | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
emwd | nawi | zld_c | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 3}
emwd | nawi | zld_c | brine_concentrator | treatment | brine_concentrator | crystallizer | waste
emwd | nawi | zld_c | crystallizer | treatment | crystallizer | landfill_zld | waste | {'approach': 'wt3'}
emwd | nawi | zld_c | municipal_drinking | use | municipal_drinking
emwd | nawi | zld_c | landfill_zld | waste | landfill_zld |  |  | {'pipe_distance': 0, 'lift_height': 400}
irwin | nawi | baseline | well_field | intake | well_field | holding_tank | outlet | {'water_type': ['brackish']}
irwin | nawi | baseline | holding_tank | treatment | holding_tank | media_filtration | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2}
irwin | nawi | baseline | media_filtration | treatment | media_filtration | hydrochloric_acid_addition | outlet | {'unit_process_name': 'media_filtration'}
irwin | nawi | baseline | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition | anti_scalant_addition | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
irwin | nawi | baseline | anti_scalant_addition | treatment | anti_scalant_addition | sodium_bisulfite_addition | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
irwin | nawi | baseline | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | electrodialysis_reversal | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 10}
irwin | nawi | baseline | electrodialysis_reversal | treatment | electrodialysis_reversal | treated_storage,water_pumping_station | outlet,waste
irwin | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
irwin | nawi | baseline | water_pumping_station | treatment | water_pumping_station | lime_softening | outlet | {'pump_type': 'treated', 'tdh': 10}
irwin | nawi | baseline | lime_softening | treatment | lime_softening | microfiltration | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
irwin | nawi | baseline | microfiltration | treatment | microfiltration | reverse_osmosis,irwin_brine_management | outlet,waste
irwin | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | municipal_drinking,irwin_brine_management | outlet,waste | {'feed_pressure': 20, 'type': 'pass', 'erd': 'no', 'pump': 'yes'}
irwin | nawi | baseline | municipal_drinking | use | municipal_drinking
irwin | nawi | baseline | irwin_brine_management | waste | irwin_brine_management
irwin | nawi | baseline | surface_discharge | waste | surface_discharge
kbhdp | nawi | baseline | well_field | intake | well_field | caustic_soda_addition,media_filtration | outlet,outlet | {'water_type': ['kbhdp_brackish_ave'], 'split_fraction': [0.393, 0.607]}
kbhdp | nawi | baseline | media_filtration | treatment | media_filtration | anti_scalant_addition | outlet
kbhdp | nawi | baseline | anti_scalant_addition | treatment | anti_scalant_addition | ro_first_stage,caustic_soda_addition | outlet,outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
kbhdp | nawi | baseline | reverse_osmosis | treatment | ro_first_stage | caustic_soda_addition,ro_second_stage | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | baseline | reverse_osmosis | treatment | ro_second_stage | media_filtration,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | baseline | caustic_soda_addition | treatment | caustic_soda_addition | chlorination | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
kbhdp | nawi | baseline | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
kbhdp | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 12}
kbhdp | nawi | baseline | deep_well_injection | waste | deep_well_injection |  |  | {'pipe_distance': 10, 'lift_height': 400}
kbhdp | nawi | baseline | municipal_drinking | use | municipal_drinking
kbhdp | nawi | baseline | surface_discharge | waste | surface_discharge
(what-if: ZLD-A: RO1 to lime softening to RO2 to evap pond + landfill)
kbhdp | nawi | zld_a | well_field | intake | well_field | caustic_soda_addition,media_filtration | outlet,outlet | {'water_type': ['kbhdp_brackish_ave'], 'split_fraction': [0.393, 0.607]}
kbhdp | nawi | zld_a | media_filtration | treatment | media_filtration | anti_scalant_addition | outlet
kbhdp | nawi | zld_a | anti_scalant_addition | treatment | anti_scalant_addition | ro_first_stage,caustic_soda_addition | outlet,outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
kbhdp | nawi | zld_a | reverse_osmosis | treatment | ro_first_stage | caustic_soda_addition,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | zld_a | basic_unit | treatment | passthrough | lime_softening | outlet | {'unit_process_name': 'passthrough'}
kbhdp | nawi | zld_a | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
kbhdp | nawi | zld_a | reverse_osmosis | treatment | ro_second_stage | caustic_soda_addition,evaporation_pond | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | zld_a | caustic_soda_addition | treatment | caustic_soda_addition | chlorination | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
kbhdp | nawi | zld_a | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
kbhdp | nawi | zld_a | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 12}
kbhdp | nawi | zld_a | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
kbhdp | nawi | zld_a | landfill_zld | waste | landfill_zld
kbhdp | nawi | zld_a | municipal_drinking | use | municipal_drinking
(what-if: ZLD-B: RO1 to lime softening to RO2 to brine concentrator to evap pond + landfill)
kbhdp | nawi | zld_b | well_field | intake | well_field | caustic_soda_addition,media_filtration | outlet,outlet | {'water_type': ['kbhdp_brackish_ave'], 'split_fraction': [0.393, 0.607]}
kbhdp | nawi | zld_b | media_filtration | treatment | media_filtration | anti_scalant_addition | outlet
kbhdp | nawi | zld_b | anti_scalant_addition | treatment | anti_scalant_addition | ro_first_stage,caustic_soda_addition | outlet,outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
kbhdp | nawi | zld_b | reverse_osmosis | treatment | ro_first_stage | caustic_soda_addition,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | zld_b | basic_unit | treatment | passthrough | lime_softening | outlet | {'unit_process_name': 'passthrough'}
kbhdp | nawi | zld_b | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
kbhdp | nawi | zld_b | reverse_osmosis | treatment | ro_second_stage | caustic_soda_addition,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | zld_b | caustic_soda_addition | treatment | caustic_soda_addition | chlorination | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
kbhdp | nawi | zld_b | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
kbhdp | nawi | zld_b | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 12}
kbhdp | nawi | zld_b | brine_concentrator | treatment | brine_concentrator | treated_storage,evaporation_pond | outlet,waste
kbhdp | nawi | zld_b | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
kbhdp | nawi | zld_b | landfill_zld | waste | landfill_zld
kbhdp | nawi | zld_b | municipal_drinking | use | municipal_drinking
(what-if: ZLD-C: RO1 to lime softening to RO2 to brine concentrator to crystallizer + landfill)
kbhdp | nawi | zld_c | well_field | intake | well_field | caustic_soda_addition,media_filtration | outlet,outlet | {'water_type': ['kbhdp_brackish_ave'], 'split_fraction': [0.393, 0.607]}
kbhdp | nawi | zld_c | media_filtration | treatment | media_filtration | anti_scalant_addition | outlet
kbhdp | nawi | zld_c | anti_scalant_addition | treatment | anti_scalant_addition | ro_first_stage,caustic_soda_addition | outlet,outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
kbhdp | nawi | zld_c | reverse_osmosis | treatment | ro_first_stage | caustic_soda_addition,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | zld_c | basic_unit | treatment | passthrough | lime_softening | outlet | {'unit_process_name': 'passthrough'}
kbhdp | nawi | zld_c | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
kbhdp | nawi | zld_c | reverse_osmosis | treatment | ro_second_stage | caustic_soda_addition,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
kbhdp | nawi | zld_c | caustic_soda_addition | treatment | caustic_soda_addition | chlorination | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
kbhdp | nawi | zld_c | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
kbhdp | nawi | zld_c | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 12}
kbhdp | nawi | zld_c | brine_concentrator | treatment | brine_concentrator | treated_storage,crystallizer | outlet,waste
kbhdp | nawi | zld_c | crystallizer | treatment | crystallizer | landfill_zld | waste | {'approach': 'wt3'}
kbhdp | nawi | zld_c | landfill_zld | waste | landfill_zld
kbhdp | nawi | zld_c | municipal_drinking | use | municipal_drinking
MUNICIPAL
big_spring | nawi | baseline | holding_tank | intake | onsite_storage | microfiltration | outlet | {'water_type': ['big_spring_feed'], 'avg_storage_time': 24, 'surge_cap': 0.2}
big_spring | nawi | baseline | microfiltration | treatment | microfiltration | reverse_osmosis | outlet
big_spring | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | uv_aop | outlet | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | baseline | uv_aop | treatment | uv_aop | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 300, 'aop': True, 'uvt_in': 0.95}
big_spring | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
big_spring | nawi | baseline | municipal_drinking | use | municipal_drinking
big_spring | nawi | baseline | surface_discharge | waste | surface_discharge
(what-if: RO1 to deep well injection. Cost and energy impacts at various injection pressures)
big_spring | nawi | dwi_a | holding_tank | intake | onsite_storage | microfiltration | outlet | {'water_type': ['big_spring_feed'], 'avg_storage_time': 24, 'surge_cap': 0.2}
big_spring | nawi | dwi_a | microfiltration | treatment | microfiltration | reverse_osmosis,deep_well_injection | outlet,waste
big_spring | nawi | dwi_a | reverse_osmosis | treatment | reverse_osmosis | uv_aop,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | dwi_a | uv_aop | treatment | uv_aop | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 300, 'aop': True, 'uvt_in': 0.95}
big_spring | nawi | dwi_a | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
big_spring | nawi | dwi_a | municipal_drinking | use | municipal_drinking
big_spring | nawi | dwi_a | deep_well_injection | waste | deep_well_injection |  |  | {'pipe_distance': 10, 'lift_height': 400}
(what-if: RO1 to ozone to BAF to lime softening to ro2 to deep well injection.)
big_spring | nawi | dwi_b | holding_tank | intake | onsite_storage | microfiltration | outlet | {'water_type': ['big_spring_feed'], 'avg_storage_time': 24, 'surge_cap': 0.2}
big_spring | nawi | dwi_b | microfiltration | treatment | microfiltration | ro_first_stage,deep_well_injection | outlet,waste
big_spring | nawi | dwi_b | reverse_osmosis | treatment | ro_first_stage | uv_aop,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | dwi_b | basic_unit | treatment | passthrough | ozone | outlet | {'unit_process_name': 'passthrough'}
big_spring | nawi | dwi_b | ozone_aop | treatment | ozone | bio_active_filtration | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False}
big_spring | nawi | dwi_b | basic_unit | treatment | bio_active_filtration | lime_softening | outlet | {'unit_process_name': 'bio_active_filtration'}
big_spring | nawi | dwi_b | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
big_spring | nawi | dwi_b | reverse_osmosis | treatment | ro_second_stage | uv_aop,deep_well_injection | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | dwi_b | uv_aop | treatment | uv_aop | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 300, 'aop': True, 'uvt_in': 0.95}
big_spring | nawi | dwi_b | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
big_spring | nawi | dwi_b | municipal_drinking | use | municipal_drinking
big_spring | nawi | dwi_b | deep_well_injection | waste | deep_well_injection |  |  | {'pipe_distance': 10, 'lift_height': 400}
big_spring | nawi | dwi_b | surface_discharge | waste | surface_discharge
(what-if: RO1 to ozone to BAF to lime softening to ro2 to evaporation pond + landfill)
big_spring | nawi | zld_a | holding_tank | intake | onsite_storage | microfiltration | outlet | {'water_type': ['big_spring_feed'], 'avg_storage_time': 24, 'surge_cap': 0.2}
big_spring | nawi | zld_a | microfiltration | treatment | microfiltration | ro_first_stage,evaporation_pond | outlet,waste
big_spring | nawi | zld_a | reverse_osmosis | treatment | ro_first_stage | uv_aop,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | zld_a | basic_unit | treatment | passthrough | ozone | outlet | {'unit_process_name': 'passthrough'}
big_spring | nawi | zld_a | ozone_aop | treatment | ozone | bio_active_filtration | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False}
big_spring | nawi | zld_a | basic_unit | treatment | bio_active_filtration | lime_softening | outlet | {'unit_process_name': 'bio_active_filtration'}
big_spring | nawi | zld_a | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
big_spring | nawi | zld_a | reverse_osmosis | treatment | ro_second_stage | uv_aop,evaporation_pond | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | zld_a | uv_aop | treatment | uv_aop | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 300, 'aop': True, 'uvt_in': 0.95}
big_spring | nawi | zld_a | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
big_spring | nawi | zld_a | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
big_spring | nawi | zld_a | municipal_drinking | use | municipal_drinking
big_spring | nawi | zld_a | landfill_zld | waste | landfill_zld
(what-if: RO1 to ozone to BAF to lime softening to ro2 to brine concentrator to evaporation pond + landfill)
big_spring | nawi | zld_b | holding_tank | intake | onsite_storage | microfiltration | outlet | {'water_type': ['big_spring_feed'], 'avg_storage_time': 24, 'surge_cap': 0.2}
big_spring | nawi | zld_b | microfiltration | treatment | microfiltration | ro_first_stage | outlet
big_spring | nawi | zld_b | reverse_osmosis | treatment | ro_first_stage | uv_aop,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | zld_b | basic_unit | treatment | passthrough | ozone | outlet | {'unit_process_name': 'passthrough'}
big_spring | nawi | zld_b | ozone_aop | treatment | ozone | bio_active_filtration | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False}
big_spring | nawi | zld_b | basic_unit | treatment | bio_active_filtration | lime_softening | outlet | {'unit_process_name': 'bio_active_filtration'}
big_spring | nawi | zld_b | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
big_spring | nawi | zld_b | reverse_osmosis | treatment | ro_second_stage | uv_aop,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | zld_b | uv_aop | treatment | uv_aop | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 300, 'aop': True, 'uvt_in': 0.95}
big_spring | nawi | zld_b | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
big_spring | nawi | zld_b | brine_concentrator | treatment | brine_concentrator | treated_storage,evaporation_pond | outlet,waste
big_spring | nawi | zld_b | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
big_spring | nawi | zld_b | municipal_drinking | use | municipal_drinking
big_spring | nawi | zld_b | landfill_zld | waste | landfill_zld
(what-if: RO1 to ozone to BAF to lime softening to ro2 to brine concentrator to crystallizer to landfill).)
big_spring | nawi | zld_c | holding_tank | intake | onsite_storage | microfiltration | outlet | {'water_type': ['big_spring_feed'], 'avg_storage_time': 24, 'surge_cap': 0.2}
big_spring | nawi | zld_c | microfiltration | treatment | microfiltration | ro_first_stage | outlet | {'unit_process_name': 'microfiltration'}
big_spring | nawi | zld_c | reverse_osmosis | treatment | ro_first_stage | uv_aop,passthrough | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | zld_c | basic_unit | treatment | passthrough | ozone | outlet | {'unit_process_name': 'passthrough'}
big_spring | nawi | zld_c | ozone_aop | treatment | ozone | bio_active_filtration | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False}
big_spring | nawi | zld_c | basic_unit | treatment | bio_active_filtration | lime_softening | outlet | {'unit_process_name': 'bio_active_filtration'}
big_spring | nawi | zld_c | lime_softening | treatment | lime_softening | ro_second_stage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
big_spring | nawi | zld_c | reverse_osmosis | treatment | ro_second_stage | uv_aop,brine_concentrator | outlet,waste | {'erd': 'no', 'pump': 'yes', 'feed_pressure': 15}
big_spring | nawi | zld_c | uv_aop | treatment | uv_aop | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 300, 'aop': True, 'uvt_in': 0.95}
big_spring | nawi | zld_c | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 6}
big_spring | nawi | zld_c | brine_concentrator | treatment | brine_concentrator | treated_storage,crystallizer | outlet,waste
big_spring | nawi | zld_c | crystallizer | treatment | crystallizer | landfill_zld | waste
big_spring | nawi | zld_c | municipal_drinking | use | municipal_drinking
big_spring | nawi | zld_c | landfill_zld | waste | landfill_zld
hrsd | nawi | baseline | water_pumping_station | intake | water_pumping_station | coag_and_floc | outlet | {'water_type': ['hrsd_municipal'], 'pump_type': 'raw', 'tdh': 10}
hrsd | nawi | baseline | coag_and_floc | treatment | coag_and_floc | sedimentation | outlet | {'alum_dose' : 10, 'polymer_dose': 0.1}
hrsd | nawi | baseline | sedimentation | treatment | sedimentation | ozonation | outlet | {'settling_velocity': 0.005}
hrsd | nawi | baseline | ozone_aop | treatment | ozonation | fixed_bed_gravity_basin | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False}
hrsd | nawi | baseline | fixed_bed_gravity_basin | treatment | fixed_bed_gravity_basin | gac_pressure_vessel | outlet
hrsd | nawi | baseline | gac_pressure_vessel | treatment | gac_pressure_vessel | uv_irradiation,sludge_tank | outlet,waste | {'ebct': 10}
hrsd | nawi | baseline | uv_aop | treatment | uv_irradiation | chlorination | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 350, 'aop': False, 'uvt_in': 0.9}
hrsd | nawi | baseline | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
hrsd | nawi | baseline | treated_storage | treatment | treated_storage | recharge_pump_well | outlet | {'hours': 6}
hrsd | nawi | baseline | basic_unit | use | recharge_pump_well |  |  | {'unit_process_name': 'recharge_pump_well'}
hrsd | nawi | baseline | basic_unit | waste | sludge_tank |  |  | {'unit_process_name': 'sludge_tank'}
ocwd | nawi | baseline | water_pumping_station | intake | water_pumping_station | microscreen_filtration,flow_equalization | outlet,outlet | {'water_type': ['ocwd_feed'], 'pump_type': 'raw', 'tdh': 10, 'split_fraction': [0.85, 0.15]}
ocwd | nawi | baseline | holding_tank | treatment | flow_equalization | microscreen_filtration | outlet | {'avg_storage_time': 12, 'surge_cap': 0}
ocwd | nawi | baseline | basic_unit | treatment | microscreen_filtration | chlorination | outlet | {'unit_process_name': 'microscreen_filtration'}
ocwd | nawi | baseline | chlorination | treatment | chlorination | microfiltration | outlet | {'chemical_name': 'Chlorine'}
ocwd | nawi | baseline | microfiltration | treatment | microfiltration | buffer_tank | outlet | {'unit_process_name': 'microfiltration'}
ocwd | nawi | baseline | basic_unit | treatment | buffer_tank | sulfuric_acid_addition | outlet | {'unit_process_name': 'buffer_tank'}
ocwd | nawi | baseline | sulfuric_acid_addition | treatment | sulfuric_acid_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 10}
ocwd | nawi | baseline | anti_scalant_addition | treatment | anti_scalant_addition | cartridge_filtration | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
ocwd | nawi | baseline | cartridge_filtration | treatment | cartridge_filtration | reverse_osmosis | outlet
ocwd | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | uv_aop | outlet | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
ocwd | nawi | baseline | uv_aop | treatment | uv_aop | decarbonator | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 350, 'aop': True, 'uvt_in': 0.95}
ocwd | nawi | baseline | basic_unit | treatment | decarbonator | lime_addition | outlet | {'unit_process_name': 'decarbonator'}
ocwd | nawi | baseline | lime_addition | treatment | lime_addition | treated_storage | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
ocwd | nawi | baseline | treated_storage | treatment | treated_storage | municipal_drinking | outlet | {'hours': 24}
ocwd | nawi | baseline | municipal_drinking | use | municipal_drinking
ocwd | nawi | baseline | surface_discharge | waste | surface_discharge
solaire | nawi | baseline | holding_tank | intake | onsite_storage | water_pumping_station | outlet | {'water_type': ['solaire_graywater', 'solaire_blackwater'], 'avg_storage_time': 24, 'surge_cap': 0}
solaire | nawi | baseline | water_pumping_station | treatment | water_pumping_station | mbr_nitrification | outlet | {'pump_type': 'raw', 'tdh': 10}
solaire | nawi | baseline | basic_unit | treatment | mbr_nitrification | ozone_aop | outlet | {'unit_process_name': 'mbr_nitrification'}
solaire | nawi | baseline | ozone_aop | treatment | ozone_aop | uv_irradiation | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': True}
solaire | nawi | baseline | uv_aop | treatment | uv_irradiation | treated_storage | outlet | {'chemical_name': 'Hydrogen_Peroxide', 'dose': 5, 'uv_dose': 350, 'aop': False, 'uvt_in': 0.95}
solaire | nawi | baseline | treated_storage | treatment | treated_storage | graywater_supply | outlet | {'hours': 3}
solaire | nawi | baseline | basic_unit | use | graywater_supply |  |  | {'unit_process_name': 'cooling_supply'}
solaire | nawi | baseline | surface_discharge | waste | surface_discharge
MINING
heap_leaching | nawi | baseline | well_field | intake | well_field | heap_leaching | outlet | {'water_type': ['ore_heap_make_up']}
heap_leaching | nawi | baseline | heap_leaching | intake | heap_leaching | agglom_stacking | outlet | {'water_type': ['ore_heap_recycle']}
heap_leaching | nawi | baseline | agglom_stacking | treatment | agglom_stacking | solution_distribution_and_recovery_plant | outlet
heap_leaching | nawi | baseline | solution_distribution_and_recovery_plant | treatment | solution_distribution_and_recovery_plant | industrial | outlet
heap_leaching | nawi | baseline | basic_unit | use | industrial |  |  | {'unit_process_name':'industrial'}
heap_leaching | nawi | baseline | surface_discharge | waste | surface_discharge
lithium | nawi | baseline | well_field | intake | well_field | evaporation_pond_a | outlet | {'water_type': ['lithium_brine']}
lithium | nawi | baseline | evaporation_pond | treatment | evaporation_pond_a | sedimentation | waste | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
lithium | nawi | baseline | sedimentation | treatment | sedimentation | evaporation_pond_b,sludge_tank | outlet,waste | {'settling_velocity': 0.005}
lithium | nawi | baseline | evaporation_pond | treatment | evaporation_pond_b | holding_tank | waste | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
lithium | nawi | baseline | holding_tank | treatment | holding_tank | industrial | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2}
lithium | nawi | baseline | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
lithium | nawi | baseline | basic_unit | waste | sludge_tank |  |  | {'unit_process_name': 'sludge_tank'}
Additional RO upstream of the evaporation pond to improve recovery. TODO: Added RO has 35% recovery
lithium_x | nawi | add_ixro | well_field | intake | well_field | ion_exchange | outlet | {'water_type': ['lithium_brine']}
lithium_x | nawi | add_ixro | anion_exchange_epa | treatment | ion_exchange | evaporation_pond_a | waste
lithium_x | nawi | add_ixro_x | reverse_osmosis | treatment | reverse_osmosis | holding_tank,evaporation_pond_a | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
lithium_x | nawi | add_ixro | evaporation_pond | treatment | evaporation_pond_a | sedimentation | waste | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
lithium_x | nawi | add_ixro | sedimentation | treatment | sedimentation | evaporation_pond_b,sludge_tank | outlet,waste | {'settling_velocity': 0.005}
lithium_x | nawi | add_ixro | evaporation_pond | treatment | evaporation_pond_b | holding_tank | waste | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
lithium_x | nawi | add_ixro | holding_tank | treatment | holding_tank | industrial | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2}
lithium_x | nawi | add_ixro | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
lithium_x | nawi | add_ixro | basic_unit | waste | sludge_tank |  |  | {'unit_process_name': 'sludge_tank'}
50% recovery from an added HPRO or brine concentrator upstream of evaporation pond to achieve 2x capacity increase. TODO: Added RO has 35% recovery
lithium | nawi | add_bc | well_field | intake | well_field | brine_concentrator | outlet | {'water_type': ['lithium_brine']}
lithium | nawi | add_bc | brine_concentrator | treatment | brine_concentrator | holding_tank,evaporation_pond_a | outlet,waste
lithium | nawi | add_bc | evaporation_pond | treatment | evaporation_pond_a | sedimentation | waste | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
lithium | nawi | add_bc | sedimentation | treatment | sedimentation | evaporation_pond_b,sludge_tank | outlet,waste | {'settling_velocity': 0.005}
lithium | nawi | add_bc | evaporation_pond | treatment | evaporation_pond_b | holding_tank | waste | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
lithium | nawi | add_bc | holding_tank | treatment | holding_tank | industrial | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2}
lithium | nawi | add_bc | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
lithium | nawi | add_bc | basic_unit | waste | sludge_tank |  |  | {'unit_process_name': 'sludge_tank'}
uranium | nawi | baseline | well_field | intake | active_mine | ion_exchange | outlet | {'water_type': ['uranium_active']}
uranium | nawi | baseline | anion_exchange_epa | treatment | ion_exchange | active_mine,ro_production | outlet,waste
uranium | nawi | baseline | reverse_osmosis | treatment | ro_production | active_mine,ro_restore | outlet,waste | {'pump': 'yes', 'feed_pressure': 25, 'erd': 'no'}
uranium | nawi | baseline | reverse_osmosis | treatment | ro_restore | restoration_mine,holding_pond | outlet,waste | {'pump': 'yes', 'feed_pressure': 25, 'erd': 'no'}
uranium | nawi | baseline | treated_storage | treatment | holding_pond | deep_well_injection | waste | {'hours': 24}
uranium | nawi | baseline | well_field | intake | restoration_mine | ro_restore_1 | outlet | {'water_type': ['uranium_restore']}
uranium | nawi | baseline | reverse_osmosis | treatment | ro_restore_1 | ro_restore,restoration_mine | outlet,waste | {'pump': 'yes', 'feed_pressure': 65, 'erd': 'no'}
uranium | nawi | baseline | deep_well_injection | waste | deep_well_injection |  |  | {'incl_piping': False, 'pipe_distance': 22}
POWER
cherokee | nawi | baseline | cooling_tower | intake | cooling_tower | holding_tank_a | outlet | {'water_type': ['cherokee_ct_makeup'], 'method': 'make_up_mass_balance', 'cycles': 6}
cherokee | nawi | baseline | holding_tank | treatment | holding_tank_a | clarifier | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2}
cherokee | nawi | baseline | basic_unit | treatment | clarifier | settling_pond,landfill | outlet,waste | {'unit_process_name': 'clarifier'}
cherokee | nawi | baseline | basic_unit | treatment | settling_pond | discharge | outlet | {'unit_process_name': 'settling_pond'}
cherokee | nawi | baseline | holding_tank | intake | holding_tank_b | media_filtration | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['denver_city_water']}
cherokee | nawi | baseline | media_filtration | treatment | media_filtration | sodium_bisulfite_addition | outlet
cherokee | nawi | baseline | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
cherokee | nawi | baseline | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
cherokee | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | treated_storage,clarifier | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
cherokee | nawi | baseline | treated_storage | treatment | treated_storage | industrial | outlet | {'hours': 3}
cherokee | nawi | baseline | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
cherokee | nawi | baseline | basic_unit | use | discharge |  |  | {'unit_process_name': 'discharge'}
cherokee | nawi | baseline | landfill | waste | landfill
(what-if: ZLD by treating CT blowdown)
cherokee | nawi | zld_ct | cooling_tower | intake | cooling_tower | holding_tank_a | outlet | {'water_type': ['cherokee_ct_makeup'], 'method': 'make_up_mass_balance', 'cycles': 6}
cherokee | nawi | zld_ct | holding_tank | treatment | holding_tank_a | clarifier | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2}
cherokee | nawi | zld_ct | basic_unit | treatment | clarifier | media_filtration_a,landfill_zld | outlet,waste | {'unit_process_name': 'clarifier'}
cherokee | nawi | zld_ct | basic_unit | treatment | media_filtration_a | reverse_osmosis_a,landfill_zld | outlet,waste | {'unit_process_name': 'media_filtration'}
cherokee | nawi | zld_ct | reverse_osmosis | treatment | reverse_osmosis_a | treated_storage_a,evaporation_pond | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
cherokee | nawi | zld_ct | treated_storage | treatment | treated_storage_a | discharge | outlet | {'hours': 3}
cherokee | nawi | zld_ct | holding_tank | intake | holding_tank_b | media_filtration_b | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['denver_city_water']}
cherokee | nawi | zld_ct | basic_unit | treatment | media_filtration_b | sodium_bisulfite_addition,landfill_zld | outlet,waste | {'unit_process_name': 'media_filtration'}
cherokee | nawi | zld_ct | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
cherokee | nawi | zld_ct | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis_b | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
cherokee | nawi | zld_ct | reverse_osmosis | treatment | reverse_osmosis_b | treated_storage_b,clarifier | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
cherokee | nawi | zld_ct | treated_storage | treatment | treated_storage_b | industrial | outlet | {'hours': 3}
cherokee | nawi | zld_ct | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
cherokee | nawi | zld_ct | basic_unit | use | discharge |  |  | {'unit_process_name': 'discharge'}
cherokee | nawi | zld_ct | landfill_zld | waste | landfill_zld
cherokee | nawi | zld_ct | evaporation_pond | waste | evaporation_pond |  |  | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 25, 'solar_rad': 25}
(what-if: ZLD with a brine concentrator instead of CCRO)
cherokee | nawi | zld_brine_conc | cooling_tower | intake | cooling_tower | holding_tank_a | outlet | {'water_type': ['cherokee_ct_makeup'], 'method': 'make_up_mass_balance', 'cycles': 6}
cherokee | nawi | zld_brine_conc | holding_tank | treatment | holding_tank_a | clarifier | outlet | {'avg_storage_time':24, 'surge_cap': 0.2}
cherokee | nawi | zld_brine_conc | basic_unit | treatment | clarifier | media_filtration_a,landfill_zld | outlet,waste | {'unit_process_name': 'clarifier'}
cherokee | nawi | zld_brine_conc | basic_unit | treatment | media_filtration_a | brine_concentrator,landfill_zld | outlet,waste | {'unit_process_name': 'media_filtration'}
cherokee | nawi | zld_brine_conc | brine_concentrator | treatment | brine_concentrator | treated_storage_a,evaporation_pond | outlet,waste
cherokee | nawi | zld_brine_conc | treated_storage | treatment | treated_storage_a | discharge | outlet | {'hours': 3}
cherokee | nawi | zld_brine_conc | holding_tank | intake | holding_tank_b | media_filtration_b | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['denver_city_water']}
cherokee | nawi | zld_brine_conc | basic_unit | treatment | media_filtration_b | sodium_bisulfite_addition,landfill_zld | outlet,waste | {'unit_process_name': 'media_filtration'}
cherokee | nawi | zld_brine_conc | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
cherokee | nawi | zld_brine_conc | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis_a | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
cherokee | nawi | zld_brine_conc | reverse_osmosis | treatment | reverse_osmosis_a | treated_storage_b,clarifier | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
cherokee | nawi | zld_brine_conc | treated_storage | treatment | treated_storage_b | industrial | outlet | {'hours': 3}
cherokee | nawi | zld_brine_conc | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
cherokee | nawi | zld_brine_conc | basic_unit | use | discharge |  |  | {'unit_process_name': 'discharge'}
cherokee | nawi | zld_brine_conc | landfill_zld | waste | landfill_zld
cherokee | nawi | zld_brine_conc | evaporation_pond | waste | evaporation_pond |  |  | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 25, 'solar_rad': 25}
gila_river | nawi | baseline | cooling_tower | intake | cooling_tower | holding_tank | outlet | {'water_type': ['gila_river_water'],'method': 'make_up_mass_balance', 'cycles': 8}
gila_river | nawi | baseline | holding_tank | treatment | holding_tank | brine_concentrator,ultra_filtration | outlet,outlet | {'avg_storage_time': 12, 'surge_cap': 0.2}
gila_river | nawi | baseline | brine_concentrator | treatment | brine_concentrator | industrial_a,evaporation_pond | outlet,waste
gila_river | nawi | baseline | evaporation_pond | treatment | evaporation_pond |  |  | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
gila_river | nawi | baseline | basic_unit | use | industrial_a |  |  | {'unit_process_name': 'industrial'}
gila_river | nawi | baseline | basic_unit | treatment | ultra_filtration | reverse_osmosis | outlet | {'unit_process_name': 'ultra_filtration'}
gila_river | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | industrial_b,evaporation_pond | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
gila_river | nawi | baseline | basic_unit | use | industrial_b |  |  | {'unit_process_name': 'industrial'}
(What-if both brine concentrators)
gila_river | nawi | both_brine | cooling_tower | intake | cooling_tower | holding_tank | outlet | {'water_type': ['gila_river_water'],'method': 'make_up_mass_balance', 'cycles': 8}
gila_river | nawi | both_brine | holding_tank | treatment | holding_tank | brine_concentrator_a,ultra_filtration | outlet,outlet | {'avg_storage_time': 12, 'surge_cap': 0.2}
gila_river | nawi | both_brine | brine_concentrator | treatment | brine_concentrator_a | industrial_a,evaporation_pond | outlet,waste
gila_river | nawi | both_brine | evaporation_pond | treatment | evaporation_pond |  |  | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
gila_river | nawi | both_brine | basic_unit | use | industrial_a |  |  | {'unit_process_name': 'industrial'}
gila_river | nawi | both_brine | basic_unit | treatment | ultra_filtration | brine_concentrator_b | outlet | {'unit_process_name': 'ultra_filtration'}
gila_river | nawi | both_brine | brine_concentrator | treatment | brine_concentrator_b | industrial_b,evaporation_pond | outlet,waste
gila_river | nawi | both_brine | basic_unit | use | industrial_b |  |  | {'unit_process_name': 'industrial'}
(What-if both RO)
gila_river | nawi | both_ro | cooling_tower | intake | cooling_tower | holding_tank | outlet | {'water_type': ['gila_river_water'],'method': 'make_up_mass_balance', 'cycles': 8}
gila_river | nawi | both_ro | holding_tank | treatment | holding_tank | reverse_osmosis_a,ultra_filtration | outlet,outlet | {'avg_storage_time': 12, 'surge_cap': 0.2}
gila_river | nawi | both_ro | reverse_osmosis | treatment | reverse_osmosis_a | industrial_a,evaporation_pond | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
gila_river | nawi | both_ro | evaporation_pond | treatment | evaporation_pond |  |  | {'approach': 'wt3', 'evap_method': 'jensen', 'air_temp': 20, 'solar_rad': 25}
gila_river | nawi | both_ro | basic_unit | use | industrial_a |  |  | {'unit_process_name': 'industrial'}
gila_river | nawi | both_ro | basic_unit | treatment | ultra_filtration | reverse_osmosis_b | outlet | {'unit_process_name': 'ultra_filtration'}
gila_river | nawi | both_ro | reverse_osmosis | treatment | reverse_osmosis_b | industrial_b,evaporation_pond | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
gila_river | nawi | both_ro | basic_unit | use | industrial_b |  |  | {'unit_process_name': 'industrial'}
AGRICULTURE
beef | nawi | baseline | basic_unit | intake | screen | dissolved_air_flotation,sludge_tank | outlet,waste | {'water_type': ['beef_processing'], 'unit_process_name': 'screen'}
beef | nawi | baseline | basic_unit | treatment | dissolved_air_flotation | anaerobic_digestion_oxidation,sludge_tank | outlet,waste | {'unit_process_name': 'dissolved_air_flotation'}
beef | nawi | baseline | basic_unit | treatment | anaerobic_digestion_oxidation | discharge,sludge_tank | outlet,waste | {'unit_process_name': 'anaerobic_digestion_oxidation'}
beef | nawi | baseline | basic_unit | use | discharge |  |  | {'unit_process_name': 'passthrough'}
beef | nawi | baseline | basic_unit | waste | sludge_tank |  |  | {'unit_process_name': 'sludge_tank'}
monterey_one | nawi | baseline_disp | water_pumping_station | intake | water_pumping_station | coag_and_floc | outlet | {'water_type': ['secondary_ww'], 'pump_type': 'raw', 'tdh': 100}
monterey_one | nawi | baseline_disp | coag_and_floc | treatment | coag_and_floc | dual_media_filtration,landfill | outlet,waste | {'alum_dose' : 10, 'polymer_dose': 0.1}
monterey_one | nawi | baseline_disp | basic_unit | treatment | dual_media_filtration | chlorination,landfill | outlet,waste | {'unit_process_name': 'dual_media_filtration'}
monterey_one | nawi | baseline_disp | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
monterey_one | nawi | baseline_disp | treated_storage | treatment | treated_storage | intrusion_mitigation | outlet | {'hours': 24}
monterey_one | nawi | baseline_disp | basic_unit | use | intrusion_mitigation |  |  | {'unit_process_name': 'intrusion_mitigation'}
monterey_one | nawi | baseline_disp | landfill | waste | landfill
monterey_one | nawi | baseline | water_pumping_station | intake | water_pumping_station | coag_and_floc | outlet | {'water_type': ['secondary_ww'], 'pump_type': 'raw', 'tdh': 100}
monterey_one | nawi | baseline | coag_and_floc | treatment | coag_and_floc | dual_media_filtration,landfill | outlet,waste | {'alum_dose' : 10, 'polymer_dose': 0.1}
monterey_one | nawi | baseline | basic_unit | treatment | dual_media_filtration | chlorination,landfill | outlet,waste | {'unit_process_name': 'dual_media_filtration'}
monterey_one | nawi | baseline | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
monterey_one | nawi | baseline | treated_storage | use | treated_storage |  |  | {'hours': 24}
monterey_one | nawi | baseline | landfill | waste | landfill
What-if: Add RO to current configuration to assess impact on costs and outlet TDS.
monterey_one | nawi | add_ro | water_pumping_station | intake | water_pumping_station | coag_and_floc | outlet | {'water_type': ['secondary_ww'], 'pump_type': 'raw', 'tdh': 10}
monterey_one | nawi | add_ro | coag_and_floc | treatment | coag_and_floc | dual_media_filtration,landfill | outlet,waste | {'alum_dose' : 10, 'polymer_dose': 0.1}
monterey_one | nawi | add_ro | basic_unit | treatment | dual_media_filtration | reverse_osmosis,landfill | outlet,waste | {'unit_process_name': 'dual_media_filtration'}
monterey_one | nawi | add_ro | reverse_osmosis | treatment | reverse_osmosis | chlorination,landfill | outlet,waste | {'pump': 'yes', 'feed_pressure': 30, 'erd': 'no'}
monterey_one | nawi | add_ro | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
monterey_one | nawi | add_ro | treated_storage | treatment | treated_storage | intrusion_mitigation | outlet | {'hours': 24}
monterey_one | nawi | add_ro | basic_unit | use | intrusion_mitigation |  |  | {'unit_process_name': 'intrusion_mitigation'}
monterey_one | nawi | add_ro | landfill | waste | landfill
Add EDR to current configuration to assess impact on costs and outlet TDS.
monterey_one | nawi | add_edr | water_pumping_station | intake | water_pumping_station | coag_and_floc | outlet | {'water_type': ['secondary_ww'], 'pump_type': 'raw', 'tdh': 10}
monterey_one | nawi | add_edr | coag_and_floc | treatment | coag_and_floc | dual_media_filtration,landfill | outlet,waste | {'alum_dose' : 10, 'polymer_dose': 0.1}
monterey_one | nawi | add_edr | basic_unit | treatment | dual_media_filtration | electrodialysis_reversal,landfill | outlet,waste | {'unit_process_name': 'dual_media_filtration'}
monterey_one | nawi | add_edr | electrodialysis_reversal | treatment | electrodialysis_reversal | chlorination,landfill | outlet,waste
monterey_one | nawi | add_edr | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
monterey_one | nawi | add_edr | treated_storage | treatment | treated_storage | intrusion_mitigation | outlet | {'hours': 24}
monterey_one | nawi | add_edr | basic_unit | use | intrusion_mitigation |  |  | {'unit_process_name': 'intrusion_mitigation'}
monterey_one | nawi | add_edr | landfill | waste | landfill
Add Ion exchange (Or other in-house desal technology) to current configuration to assess impact on costs and outlet TDS.
monterey_one | nawi | add_ix | water_pumping_station | intake | water_pumping_station | coag_and_floc | outlet | {'water_type': ['secondary_ww'], 'pump_type': 'raw', 'tdh': 10}
monterey_one | nawi | add_ix | coag_and_floc | treatment | coag_and_floc | dual_media_filtration,landfill | outlet,waste | {'alum_dose' : 10, 'polymer_dose': 0.1}
monterey_one | nawi | add_ix | basic_unit | treatment | dual_media_filtration | ion_exchange,landfill | outlet,waste | {'unit_process_name': 'dual_media_filtration'}
monterey_one | nawi | add_ix | anion_exchange_epa | treatment | ion_exchange | chlorination,landfill | outlet,waste | {'tds_in': 15}
monterey_one | nawi | add_ix | chlorination | treatment | chlorination | treated_storage | outlet | {'chemical_name': 'Chlorine'}
monterey_one | nawi | add_ix | treated_storage | treatment | treated_storage | intrusion_mitigation | outlet | {'hours': 24}
monterey_one | nawi | add_ix | basic_unit | use | intrusion_mitigation |  |  | {'unit_process_name': 'intrusion_mitigation'}
monterey_one | nawi | add_ix | landfill | waste | landfill
san_luis | nawi | baseline | basic_unit | intake | feed_water_tank | drainage_sump_pump1 | outlet | {'water_type':['irrigation_and_drainage'], 'unit_process_name': 'feed_water_tank'}
san_luis | nawi | baseline | basic_unit | treatment | drainage_sump_pump1 | drainage_sump_pump2 | outlet | {'unit_process_name': 'drainage_sump_pump1'}
san_luis | nawi | baseline | basic_unit | treatment | drainage_sump_pump2 | raw_water_pump1 | outlet | {'unit_process_name': 'drainage_sump_pump2'}
san_luis | nawi | baseline | basic_unit | treatment | raw_water_pump1 | raw_water_pump2 | outlet | {'unit_process_name': 'raw_water_pump1'}
san_luis | nawi | baseline | basic_unit | treatment | raw_water_pump2 | sodium_hypochlorite_1 | outlet | {'unit_process_name': 'raw_water_pump2'}
san_luis | nawi | baseline | chemical_addition | treatment | sodium_hypochlorite_1 | molasses_addition | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 1}
san_luis | nawi | baseline | chemical_addition | treatment | molasses_addition | glycerin_addition | outlet | {'chemical_name': 'Molasses', 'dose': 5}
san_luis | nawi | baseline | chemical_addition | treatment | glycerin_addition | hydrochloric_acid_addition_1 | outlet | {'chemical_name': 'Glycerin (C3H8O3)', 'dose': 4}
san_luis | nawi | baseline | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_1 | bioreactor_feed_pump | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | baseline | basic_unit | treatment | bioreactor_feed_pump | bioreactor_feed_pump_2 | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | baseline | basic_unit | treatment | bioreactor_feed_pump_2 | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | baseline | basic_unit | treatment | abmet_interstage_pump | abmet_interstage_pump_2 | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | baseline | basic_unit | treatment | abmet_interstage_pump_2 | abmet_intermediate_pump | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | baseline | basic_unit | treatment | abmet_intermediate_pump | abmet_intermediate_pump_2 | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | baseline | basic_unit | treatment | abmet_intermediate_pump_2 | bioreactor | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | baseline | basic_unit | treatment | bioreactor | bioreactor_effluent_pump,bioreactor_bw_pump | outlet,waste | {'unit_process_name': 'bioreactor'}
san_luis | nawi | baseline | basic_unit | treatment | bioreactor_effluent_pump | bioreactor_effluent_pump_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | baseline | basic_unit | treatment | bioreactor_effluent_pump_2 | sodium_hypochlorite_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | baseline | basic_unit | treatment | bioreactor_bw_pump | smp | waste | {'unit_process_name': 'bioreactor_bw_pump'}
san_luis | nawi | baseline | chemical_addition | treatment | sodium_hypochlorite_2 | uf_feed_pump | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 9.5}
san_luis | nawi | baseline | basic_unit | treatment | uf_feed_pump | ultra_filtration | outlet | {'unit_process_name': 'uf_feed_pump'}
san_luis | nawi | baseline | basic_unit | treatment | ultra_filtration | hydrochloric_acid_addition_2,smp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
san_luis | nawi | baseline | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_2 | sodium_bisulfite_addition | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | baseline | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
san_luis | nawi | baseline | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
san_luis | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | agriculture,smp | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | baseline | basic_unit | use | agriculture |  |  | {'unit_process_name': 'passthrough'}
san_luis | nawi | baseline | basic_unit | waste | smp |  |  | {'unit_process_name': 'smp'}
san_luis | nawi | dwi | basic_unit | intake | feed_water_tank | drainage_sump_pump1 | outlet | {'water_type':['irrigation_and_drainage'], 'unit_process_name': 'feed_water_tank'}
san_luis | nawi | dwi | basic_unit | treatment | drainage_sump_pump1 | drainage_sump_pump2 | outlet | {'unit_process_name': 'drainage_sump_pump1'}
san_luis | nawi | dwi | basic_unit | treatment | drainage_sump_pump2 | raw_water_pump1 | outlet | {'unit_process_name': 'drainage_sump_pump2'}
san_luis | nawi | dwi | basic_unit | treatment | raw_water_pump1 | raw_water_pump2 | outlet | {'unit_process_name': 'raw_water_pump1'}
san_luis | nawi | dwi | basic_unit | treatment | raw_water_pump2 | sodium_hypochlorite_1 | outlet | {'unit_process_name': 'raw_water_pump2'}
san_luis | nawi | dwi | chemical_addition | treatment | sodium_hypochlorite_1 | molasses_addition | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 1}
san_luis | nawi | dwi | chemical_addition | treatment | molasses_addition | glycerin_addition | outlet | {'chemical_name': 'Molasses', 'dose': 5}
san_luis | nawi | dwi | chemical_addition | treatment | glycerin_addition | hydrochloric_acid_addition_1 | outlet | {'chemical_name': 'Glycerin (C3H8O3)', 'dose': 4}
san_luis | nawi | dwi | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_1 | bioreactor_feed_pump | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | dwi | basic_unit | treatment | bioreactor_feed_pump | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | dwi | basic_unit | treatment | bioreactor_feed_pump_2 | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | dwi | basic_unit | treatment | abmet_interstage_pump | abmet_interstage_pump_2 | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | dwi | basic_unit | treatment | abmet_interstage_pump_2 | abmet_intermediate_pump | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | dwi | basic_unit | treatment | abmet_intermediate_pump | abmet_intermediate_pump_2 | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | dwi | basic_unit | treatment | abmet_intermediate_pump_2 | bioreactor | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | dwi | basic_unit | treatment | bioreactor | bioreactor_effluent_pump,bioreactor_bw_pump | outlet,waste | {'unit_process_name': 'bioreactor'}
san_luis | nawi | dwi | basic_unit | treatment | bioreactor_effluent_pump | bioreactor_effluent_pump_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | dwi | basic_unit | treatment | bioreactor_effluent_pump_2 | sodium_hypochlorite_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | dwi | basic_unit | treatment | bioreactor_bw_pump | deep_well_injection | waste | {'unit_process_name': 'bioreactor_bw_pump'}
san_luis | nawi | dwi | chemical_addition | treatment | sodium_hypochlorite_2 | uf_feed_pump | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 9.5}
san_luis | nawi | dwi | basic_unit | treatment | uf_feed_pump | ultra_filtration | outlet | {'unit_process_name': 'uf_feed_pump'}
san_luis | nawi | dwi | basic_unit | treatment | ultra_filtration | hydrochloric_acid_addition_2,deep_well_injection | outlet,waste | {'unit_process_name': 'ultra_filtration'}
san_luis | nawi | dwi | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_2 | sodium_bisulfite_addition | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | dwi | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
san_luis | nawi | dwi | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
san_luis | nawi | dwi | reverse_osmosis | treatment | reverse_osmosis | agriculture,deep_well_injection | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | dwi | basic_unit | use | agriculture |  |  | {'unit_process_name': 'agriculture'}
san_luis | nawi | dwi | deep_well_injection | waste | deep_well_injection |  |  | {'incl_piping': False, 'pipe_distance': 22}
what-if: Boron Treatment at demonstration scale and 1.5 MGD (0.0657 m3/s) scale. Bioreactor _ Ultrafiltration _ SWRO _ pH adjustment _ BWRO For this scenario, we would like to try a 2-stage RO process with pH adjustment. Instead of the SWRO and BWRO being in parallel (like the SLDP treatment train), we would like the SWRO and BWRO to be in series. Before the BWRO process, the pH will need to be adjusted to between 10.5 and 11"
san_luis | nawi | stage_1p5mgd | basic_unit | intake | feed_water_tank | drainage_sump_pump1 | outlet | {'water_type':['irrigation_and_drainage'], 'unit_process_name': 'feed_water_tank'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | drainage_sump_pump1 | drainage_sump_pump2 | outlet | {'unit_process_name': 'drainage_sump_pump1'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | drainage_sump_pump2 | raw_water_pump1 | outlet | {'unit_process_name': 'drainage_sump_pump2'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | raw_water_pump1 | raw_water_pump2 | outlet | {'unit_process_name': 'raw_water_pump1'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | raw_water_pump2 | sodium_hypochlorite_1 | outlet | {'unit_process_name': 'raw_water_pump2'}
san_luis | nawi | stage_1p5mgd | chemical_addition | treatment | sodium_hypochlorite_1 | molasses_addition | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 1}
san_luis | nawi | stage_1p5mgd | chemical_addition | treatment | molasses_addition | glycerin_addition | outlet | {'chemical_name': 'Molasses', 'dose': 5}
san_luis | nawi | stage_1p5mgd | chemical_addition | treatment | glycerin_addition | hydrochloric_acid_addition_1 | outlet | {'chemical_name': 'Glycerin (C3H8O3)', 'dose': 4}
san_luis | nawi | stage_1p5mgd | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_1 | bioreactor_feed_pump | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | bioreactor_feed_pump | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | bioreactor_feed_pump_2 | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | abmet_interstage_pump | abmet_interstage_pump_2 | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | abmet_interstage_pump_2 | abmet_intermediate_pump | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | abmet_intermediate_pump | abmet_intermediate_pump_2 | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | abmet_intermediate_pump_2 | bioreactor | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | bioreactor | bioreactor_effluent_pump,bioreactor_bw_pump | outlet,waste | {'unit_process_name': 'bioreactor'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | bioreactor_effluent_pump | bioreactor_effluent_pump_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | bioreactor_effluent_pump_2 | sodium_hypochlorite_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | bioreactor_bw_pump | smp | waste | {'unit_process_name': 'bioreactor_bw_pump'}
san_luis | nawi | stage_1p5mgd | chemical_addition | treatment | sodium_hypochlorite_2 | uf_feed_pump | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 9.5}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | uf_feed_pump | ultra_filtration | outlet | {'unit_process_name': 'uf_feed_pump'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | ultra_filtration | hydrochloric_acid_addition_2,smp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
san_luis | nawi | stage_1p5mgd | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_2 | sodium_bisulfite_addition | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | stage_1p5mgd | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
san_luis | nawi | stage_1p5mgd | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis_a | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
san_luis | nawi | stage_1p5mgd | reverse_osmosis | treatment | reverse_osmosis_a | agriculture,ph_adjustment | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | stage_1p5mgd | basic_unit | treatment | ph_adjustment | reverse_osmosis_b | outlet | {'unit_process_name': 'passthrough'}
san_luis | nawi | stage_1p5mgd | reverse_osmosis | treatment | reverse_osmosis_b | agriculture,smp | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | stage_1p5mgd | basic_unit | use | agriculture |  |  | {'unit_process_name': 'agriculture'}
san_luis | nawi | stage_1p5mgd | basic_unit | waste | smp |  |  | {'unit_process_name': 'smp'}
what-if: Boron Treatment at demonstration scale and 1.5 MGD (0.0657 m3/s) scale. Bioreactor _ Nanofiltration _ SWRO _ pH adjustment _ BWRO This scenario uses nanofiltration instead of ultrafiltration to remove more constituents to prevent scaling and fouling on the RO membranes."
san_luis | nawi | stage_1p5mgd_nano | basic_unit | intake | feed_water_tank | drainage_sump_pump1 | outlet | {'water_type':['irrigation_and_drainage'], 'unit_process_name': 'feed_water_tank'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | drainage_sump_pump1 | drainage_sump_pump2 | outlet | {'unit_process_name': 'drainage_sump_pump1'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | drainage_sump_pump2 | raw_water_pump1 | outlet | {'unit_process_name': 'drainage_sump_pump2'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | raw_water_pump1 | raw_water_pump2 | outlet | {'unit_process_name': 'raw_water_pump1'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | raw_water_pump2 | sodium_hypochlorite_1 | outlet | {'unit_process_name': 'raw_water_pump2'}
san_luis | nawi | stage_1p5mgd_nano | chemical_addition | treatment | sodium_hypochlorite_1 | molasses_addition | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 1}
san_luis | nawi | stage_1p5mgd_nano | chemical_addition | treatment | molasses_addition | glycerin_addition | outlet | {'chemical_name': 'Molasses', 'dose': 5}
san_luis | nawi | stage_1p5mgd_nano | chemical_addition | treatment | glycerin_addition | hydrochloric_acid_addition_1 | outlet | {'chemical_name': 'Glycerin (C3H8O3)', 'dose': 4}
san_luis | nawi | stage_1p5mgd_nano | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_1 | bioreactor_feed_pump | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | bioreactor_feed_pump | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | bioreactor_feed_pump_2 | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | abmet_interstage_pump | abmet_interstage_pump_2 | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | abmet_interstage_pump_2 | abmet_intermediate_pump | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | abmet_intermediate_pump | abmet_intermediate_pump_2 | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | abmet_intermediate_pump_2 | bioreactor | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | bioreactor | bioreactor_effluent_pump,bioreactor_bw_pump | outlet,waste | {'unit_process_name': 'bioreactor'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | bioreactor_effluent_pump | bioreactor_effluent_pump_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | bioreactor_effluent_pump_2 | sodium_hypochlorite_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | bioreactor_bw_pump | smp | waste | {'unit_process_name': 'bioreactor_bw_pump'}
san_luis | nawi | stage_1p5mgd_nano | chemical_addition | treatment | sodium_hypochlorite_2 | nano_feed_pump | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 9.5}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | nano_feed_pump | nano_filtration | outlet | {'unit_process_name': 'uf_feed_pump'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | nano_filtration | hydrochloric_acid_addition_2,smp | outlet,waste | {'unit_process_name': 'nano_filtration'}
san_luis | nawi | stage_1p5mgd_nano | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_2 | sodium_bisulfite_addition | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | stage_1p5mgd_nano | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
san_luis | nawi | stage_1p5mgd_nano | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis_a | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
san_luis | nawi | stage_1p5mgd_nano | reverse_osmosis | treatment | reverse_osmosis_a | agriculture,ph_adjustment | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | treatment | ph_adjustment | reverse_osmosis_b | outlet | {'unit_process_name': 'passthrough'}
san_luis | nawi | stage_1p5mgd_nano | reverse_osmosis | treatment | reverse_osmosis_b | agriculture,smp | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | use | agriculture |  |  | {'unit_process_name': 'agriculture'}
san_luis | nawi | stage_1p5mgd_nano | basic_unit | waste | smp |  |  | {'unit_process_name': 'smp'}
what-if: Boron Treatment at demonstration scale and 1.5 MGD (0.0657 m3/s) scale. Bioreactor _ Electrodialysis _ SWRO _ pH adjustment _ BWRO This scenario uses electrodialysis instead of ultrafiltration for better pre-treatment before the RO processes."
san_luis | nawi | stage_1p5mgd_edr | basic_unit | intake | feed_water_tank | drainage_sump_pump1 | outlet | {'water_type':['irrigation_and_drainage'], 'unit_process_name': 'feed_water_tank'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | drainage_sump_pump1 | drainage_sump_pump2 | outlet | {'unit_process_name': 'drainage_sump_pump1'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | drainage_sump_pump2 | raw_water_pump1 | outlet | {'unit_process_name': 'drainage_sump_pump2'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | raw_water_pump1 | raw_water_pump2 | outlet | {'unit_process_name': 'raw_water_pump1'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | raw_water_pump2 | sodium_hypochlorite_1 | outlet | {'unit_process_name': 'raw_water_pump2'}
san_luis | nawi | stage_1p5mgd_edr | chemical_addition | treatment | sodium_hypochlorite_1 | molasses_addition | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 1}
san_luis | nawi | stage_1p5mgd_edr | chemical_addition | treatment | molasses_addition | glycerin_addition | outlet | {'chemical_name': 'Molasses', 'dose': 5}
san_luis | nawi | stage_1p5mgd_edr | chemical_addition | treatment | glycerin_addition | hydrochloric_acid_addition_1 | outlet | {'chemical_name': 'Glycerin (C3H8O3)', 'dose': 4}
san_luis | nawi | stage_1p5mgd_edr | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_1 | bioreactor_feed_pump | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | bioreactor_feed_pump | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | bioreactor_feed_pump_2 | abmet_interstage_pump | outlet | {'unit_process_name': 'bioreactor_feed_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | abmet_interstage_pump | abmet_interstage_pump_2 | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | abmet_interstage_pump_2 | abmet_intermediate_pump | outlet | {'unit_process_name': 'abmet_interstage_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | abmet_intermediate_pump | abmet_intermediate_pump_2 | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | abmet_intermediate_pump_2 | bioreactor | outlet | {'unit_process_name': 'abmet_intermediate_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | bioreactor | bioreactor_effluent_pump,bioreactor_bw_pump | outlet,waste | {'unit_process_name': 'bioreactor'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | bioreactor_effluent_pump | bioreactor_effluent_pump_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | bioreactor_effluent_pump_2 | sodium_hypochlorite_2 | outlet | {'unit_process_name': 'bioreactor_effluent_pump'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | bioreactor_bw_pump | smp | waste | {'unit_process_name': 'bioreactor_bw_pump'}
san_luis | nawi | stage_1p5mgd_edr | chemical_addition | treatment | sodium_hypochlorite_2 | uf_feed_pump | outlet | {'chemical_name': 'Sodium Hypochlorite (NaOCl) (15%)', 'dose': 9.5}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | uf_feed_pump | electrodialysis_reversal | outlet | {'unit_process_name': 'uf_feed_pump'}
san_luis | nawi | stage_1p5mgd_edr | electrodialysis_reversal | treatment | electrodialysis_reversal | hydrochloric_acid_addition_2,smp | outlet,waste
san_luis | nawi | stage_1p5mgd_edr | hydrochloric_acid_addition | treatment | hydrochloric_acid_addition_2 | sodium_bisulfite_addition | outlet | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 10}
san_luis | nawi | stage_1p5mgd_edr | sodium_bisulfite_addition | treatment | sodium_bisulfite_addition | anti_scalant_addition | outlet | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01}
san_luis | nawi | stage_1p5mgd_edr | anti_scalant_addition | treatment | anti_scalant_addition | reverse_osmosis_a | outlet | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5}
san_luis | nawi | stage_1p5mgd_edr | reverse_osmosis | treatment | reverse_osmosis_a | agriculture,ph_adjustment | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | treatment | ph_adjustment | reverse_osmosis_b | outlet | {'unit_process_name': 'passthrough'}
san_luis | nawi | stage_1p5mgd_edr | reverse_osmosis | treatment | reverse_osmosis_b | agriculture,smp | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | use | agriculture |  |  | {'unit_process_name': 'agriculture'}
san_luis | nawi | stage_1p5mgd_edr | basic_unit | waste | smp |  |  | {'unit_process_name': 'smp'}
Agricultural | San_Luis | scale up | Scale-up the demonstration treatment facility to 1.5 MGD inlet. |  | 1.5 MGD = | 0.0657 | m3/s
Agricultural | San_Luis | scale up | Scale-up the demonstration treatment facility to 3.0 MGD inlet. |  | 3 MGD = | 0.1314 | m3/s
Agricultural | San_Luis | scale up | Scale-up the demonstration treatment facility to 5.0 MGD inlet. |  | 5 MGD = | 0.2191 | m3/s
INDUSTRIAL
iron_and_steel | nawi | baseline | well_field | intake | well_field | raw_water_pump1 | outlet | {'water_type': ['steel_oily_ww']}
iron_and_steel | nawi | baseline | basic_unit | treatment | raw_water_pump1 | primary_separator | outlet | {'unit_process_name': 'raw_water_pump1'}
iron_and_steel | nawi | baseline | basic_unit | treatment | primary_separator | coagulant_addition,raw_water_pump1_2,tramp_oil_tank | outlet,outlet,waste | {'unit_process_name': 'primary_separator', 'split_fraction': [0.83, 0.17]}
iron_and_steel | nawi | baseline | coagulant_addition | intake | coagulant_addition | coag_and_floc | outlet | {'chemical_name': ['Iron_FeCl3'], 'dose': 30, 'water_type': ['hot_mill_blowdown']}
iron_and_steel | nawi | baseline | coag_and_floc | treatment | coag_and_floc | caustic_soda_addition | outlet | {'alum_dose' : 10, 'polymer_dose': 0.1}
iron_and_steel | nawi | baseline | caustic_soda_addition | treatment | caustic_soda_addition | dissolved_air_flotation | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30}
iron_and_steel | nawi | baseline | basic_unit | treatment | dissolved_air_flotation | treated_storage | outlet | {'unit_process_name': 'air_flotation'}
iron_and_steel | nawi | baseline | treated_storage | treatment | treated_storage | discharge | outlet | {'hours': 1}
iron_and_steel | nawi | baseline | basic_unit | use | discharge |  |  | {'unit_process_name': 'discharge'}
iron_and_steel | nawi | baseline | basic_unit | waste | tramp_oil_tank |  |  | {'unit_process_name': 'tramp_oil_tank'}
iron_and_steel | nawi | baseline | basic_unit | intake | raw_water_pump1_2 | buffer_tank | outlet | {'water_type': ['steel_metal_ww'], 'unit_process_name': 'raw_water_pump1'}
iron_and_steel | nawi | baseline | basic_unit | treatment | buffer_tank | caustic_soda_addition_2 | outlet | {'unit_process_name': 'buffer_tank'}
iron_and_steel | nawi | baseline | caustic_soda_addition | treatment | caustic_soda_addition_2 | lime_addition_2 | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 3}
iron_and_steel | nawi | baseline | lime_addition | treatment | lime_addition_2 | aeration_tank | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
iron_and_steel | nawi | baseline | basic_unit | treatment | aeration_tank | coagulant_addition_2 | outlet | {'unit_process_name': 'aeration_tank'}
iron_and_steel | nawi | baseline | coagulant_addition | intake | coagulant_addition_2 | lime_addition_3 | outlet | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 30, 'water_type': ['hot_mill_blowdown_b']}
iron_and_steel | nawi | baseline | lime_addition | treatment | lime_addition_3 | clarifier | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3}
iron_and_steel | nawi | baseline | basic_unit | treatment | clarifier | treated_storage_2,landfill | outlet,waste | {'unit_process_name': 'clarifier'}
iron_and_steel | nawi | baseline | treated_storage | treatment | treated_storage_2 | discharge_2 | outlet | {'hours': 1}
iron_and_steel | nawi | baseline | basic_unit | use | discharge_2 |  |  | {'unit_process_name': 'discharge'}
iron_and_steel | nawi | baseline | landfill | waste | landfill
pulp_and_paper | nawi | baseline | basic_unit | intake | raw_water_pump1 | sedimentation | outlet | {'unit_process_name': 'raw_water_pump1', 'water_type': ['main_sewer']}
pulp_and_paper | nawi | baseline | sedimentation | treatment | sedimentation | aeration_basin1,sludge_tank | outlet,waste | {'settling_velocity': 0.005}
pulp_and_paper | nawi | baseline | basic_unit | intake | aeration_basin1 | aeration_basin2 | outlet | {'unit_process_name': 'aeration_basin1', 'water_type': ['corrosive_sewer']}
pulp_and_paper | nawi | baseline | basic_unit | treatment | aeration_basin2 | discharge | outlet | {'unit_process_name': 'aeration_basin2'}
pulp_and_paper | nawi | baseline | basic_unit | use | discharge |  |  | {'unit_process_name': 'discharge'}
pulp_and_paper | nawi | baseline | basic_unit | waste | sludge_tank |  |  | {'unit_process_name': 'sludge_tank'}
upw_x | nawi | baseline | reverse_osmosis | intake | brine_ro | treated_storage,municipal_wwtp | outlet,waste | {'pump': 'yes', 'type': 'pass', 'pass': 'first', 'feed_pressure': 85, 'erd': 'no', 'water_type': ['upw_brine']}
upw_x | nawi | baseline | treated_storage | treatment | treated_storage | industrial | outlet | {'hours': 24}
upw_x | nawi | baseline | holding_tank | intake | holding_tank | media_filtration,media_filtration_2 | outlet,outlet | {'avg_storage_time': 24, 'surge_cap': 0.2,'water_type': ['fab25']}
upw_x | nawi | baseline | basic_unit | treatment | media_filtration | uv_aop | outlet | {'unit_process_name': 'media_filtration'}
upw_x | nawi | baseline | uv_aop | treatment | uv_aop | gac_gravity | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'}
upw_x | nawi | baseline | gac_gravity | treatment | gac_gravity | ultra_filtration | outlet | {'ebct': 30}
upw_x | nawi | baseline | basic_unit | treatment | ultra_filtration | treated_storage_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw_x | nawi | baseline | treated_storage | treatment | treated_storage_2 | industrial_2 | outlet | {'hours': 24}
upw_x | nawi | baseline | basic_unit | treatment | media_filtration_2 | ultra_filtration_2 | outlet | {'unit_process_name': 'media_filtration'}
upw_x | nawi | baseline | basic_unit | treatment | ultra_filtration_2 | gac_gravity_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw_x | nawi | baseline | gac_gravity | treatment | gac_gravity_2 | reverse_osmosis | outlet | {'ebct': 30}
upw_x | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | treated_storage_3,municipal_wwtp | outlet,waste | {'pump': 'yes', 'type': 'pass', 'pass': 'first', 'membrane_area': 500000, 'feed_pressure': 85, 'erd': 'no'}
upw_x | nawi | baseline | treated_storage | treatment | treated_storage_3 | cooling_supply | outlet | {'hours': 24}
upw_x | nawi | baseline | basic_unit | use | cooling_supply |  |  | {'unit_process_name': 'cooling_supply'}
upw_x | nawi | baseline | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
upw_x | nawi | baseline | basic_unit | use | industrial_2 |  |  | {'unit_process_name': 'industrial'}
upw_x | nawi | baseline | basic_unit | waste | municipal_wwtp |  |  | {'unit_process_name': 'municipal_wwtp'}
upw | nawi | baseline | holding_tank | intake | holding_tank | media_filtration | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2,'water_type': ['fab25']}
upw | nawi | baseline | media_filtration | treatment | media_filtration | reverse_osmosis,ozone | outlet,waste
upw | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | ozone,fab_25,ro_stage | outlet,outlet,waste | {'pump': 'yes', 'erd': 'no', 'feed_pressure': 85, 'split_fraction': [.11, 0.89]}
upw | nawi | baseline | reverse_osmosis | treatment | ro_stage | reverse_osmosis,media_filtration_2 | outlet,waste | {'pump': 'yes', 'erd': 'no', 'feed_pressure': 85}
upw_x | nawi | baseline | ozone_aop | treatment | ozone | media_filtration_2 | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False}
upw | nawi | baseline | media_filtration | treatment | media_filtration_2 | uv_aop,municipal_wwtp | outlet,waste
upw | nawi | baseline | uv_aop | treatment | uv_aop | gac_gravity | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'}
upw | nawi | baseline | gac_gravity | treatment | gac_gravity | ultra_filtration,municipal_wwtp | outlet,waste | {'ebct': 30}
upw | nawi | baseline | basic_unit | treatment | ultra_filtration | media_filtration,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | baseline | basic_unit | treatment | fab_25 | ozone,media_filtration_3 | outlet,outlet | {'unit_process_name': 'passthrough', 'split_fraction': [.5, 0.5]}
upw | nawi | baseline | media_filtration | treatment | media_filtration_3 | ultra_filtration_2,municipal_wwtp | outlet,waste
upw | nawi | baseline | basic_unit | treatment | ultra_filtration_2 | gac_gravity_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | baseline | gac_gravity | treatment | gac_gravity_2 | reverse_osmosis_2,municipal_wwtp | outlet,waste | {'ebct': 30}
upw | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis_2 | cooling_supply,municipal_wwtp | outlet,waste | {'pump': 'yes', 'erd': 'no', 'feed_pressure': 85}
upw | nawi | baseline | basic_unit | use | cooling_supply |  |  | {'unit_process_name': 'cooling_supply'}
upw | nawi | baseline | basic_unit | waste | municipal_wwtp |  |  | {'unit_process_name': 'municipal_wwtp'}
(what-if: ZLD-A: RO1 > Lime Softening > RO2 > Evaporation Pond + Landfill)
upw | nawi | zld_a | reverse_osmosis | intake | brine_ro | treated_storage,municipal_wwtp | outlet,waste | {'pump': 'yes','feed_pressure': 85, 'erd': 'no', 'water_type': ['upw_brine']}
upw | nawi | zld_a | treated_storage | treatment | treated_storage | industrial | outlet | {'hours': 24}
upw | nawi | zld_a | holding_tank | intake | holding_tank | media_filtration,media_filtration_2 | outlet,outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['fab25']}
upw | nawi | zld_a | basic_unit | treatment | media_filtration | uv_aop | outlet | {'unit_process_name': 'media_filtration'}
upw | nawi | zld_a | uv_aop | treatment | uv_aop | gac_gravity | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'}
upw | nawi | zld_a | gac_gravity | treatment | gac_gravity | ultra_filtration | outlet | {'ebct': 30}
upw | nawi | zld_a | basic_unit | treatment | ultra_filtration | treated_storage_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | zld_a | treated_storage | treatment | treated_storage_2 | industrial_2 | outlet | {'hours': 24}
upw | nawi | zld_a | basic_unit | treatment | media_filtration_2 | ultra_filtration_2 | outlet | {'unit_process_name': 'media_filtration'}
upw | nawi | zld_a | basic_unit | treatment | ultra_filtration_2 | gac_gravity_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | zld_a | gac_gravity | treatment | gac_gravity_2 | ro_first_pass | outlet | {'ebct': 30}
upw | nawi | zld_a | reverse_osmosis | treatment | ro_first_pass | treated_storage_3,passthrough | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
upw | nawi | zld_a | basic_unit | treatment | passthrough | lime_softening | outlet | {'unit_process_name': 'passthrough'}
upw | nawi | zld_a | lime_softening | treatment | lime_softening | ro_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
upw | nawi | zld_a | reverse_osmosis | treatment | ro_second_pass | treated_storage_3,evaporation_pond | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
upw | nawi | zld_a | treated_storage | treatment | treated_storage_3 | cooling_supply | outlet | {'hours': 24}
upw | nawi | zld_a | basic_unit | use | cooling_supply |  |  | {'unit_process_name': 'cooling_supply'}
upw | nawi | zld_a | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
upw | nawi | zld_a | basic_unit | use | industrial_2 |  |  | {'unit_process_name': 'industrial'}
upw | nawi | zld_a | basic_unit | waste | municipal_wwtp |  |  | {'unit_process_name': 'municipal_wwtp'}
upw | nawi | zld_a | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
upw | nawi | zld_a | landfill_zld | waste | landfill_zld |  |  | {'pipe_distance': 0, 'lift_height': 400}
(what-if: ZLD-B: RO1 > Lime Softening > RO2 > Brine Concentrator > Evaporation Pond + Landfill)
upw | nawi | zld_b | reverse_osmosis | intake | brine_ro | treated_storage,municipal_wwtp | outlet,waste | {'pump': 'yes','feed_pressure': 85, 'erd': 'no', 'water_type': ['upw_brine']}
upw | nawi | zld_b | treated_storage | treatment | treated_storage | industrial | outlet | {'hours': 24}
upw | nawi | zld_b | holding_tank | intake | holding_tank | media_filtration,media_filtration_2 | outlet,outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['fab25']}
upw | nawi | zld_b | basic_unit | treatment | media_filtration | uv_aop | outlet | {'unit_process_name': 'media_filtration'}
upw | nawi | zld_b | uv_aop | treatment | uv_aop | gac_gravity | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'}
upw | nawi | zld_b | gac_gravity | treatment | gac_gravity | ultra_filtration | outlet | {'ebct': 30}
upw | nawi | zld_b | basic_unit | treatment | ultra_filtration | treated_storage_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | zld_b | treated_storage | treatment | treated_storage_2 | industrial_2 | outlet | {'hours': 24}
upw | nawi | zld_b | basic_unit | treatment | media_filtration_2 | ultra_filtration_2 | outlet | {'unit_process_name': 'media_filtration'}
upw | nawi | zld_b | basic_unit | treatment | ultra_filtration_2 | gac_gravity_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | zld_b | gac_gravity | treatment | gac_gravity_2 | ro_first_pass | outlet | {'ebct': 30}
upw | nawi | zld_b | reverse_osmosis | treatment | ro_first_pass | treated_storage,passthrough | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
upw | nawi | zld_b | basic_unit | treatment | passthrough | lime_softening | outlet | {'unit_process_name': 'passthrough'}
upw | nawi | zld_b | lime_softening | treatment | lime_softening | ro_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
upw | nawi | zld_b | reverse_osmosis | treatment | ro_second_pass | treated_storage_3,brine_concentrator | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
upw | nawi | zld_b | treated_storage | treatment | treated_storage_3 | cooling_supply | outlet | {'hours': 3}
upw | nawi | zld_b | brine_concentrator | treatment | brine_concentrator | evaporation_pond | waste
upw | nawi | zld_b | basic_unit | use | cooling_supply |  |  | {'unit_process_name': 'cooling_supply'}
upw | nawi | zld_b | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
upw | nawi | zld_b | basic_unit | use | industrial_2 |  |  | {'unit_process_name': 'industrial'}
upw | nawi | zld_b | basic_unit | waste | municipal_wwtp |  |  | {'unit_process_name': 'municipal_wwtp'}
upw | nawi | zld_b | evaporation_pond | treatment | evaporation_pond | landfill_zld | waste | {'approach': 'wt3'}
upw | nawi | zld_b | landfill_zld | waste | landfill_zld |  |  | {'pipe_distance': 0, 'lift_height': 400}
(what-if: ZLD-C: RO1 > Lime Softening > RO2 > Brine Concentrator > Crystallizer > Landfill)
upw | nawi | zld_c | reverse_osmosis | intake | brine_ro | treated_storage,municipal_wwtp | outlet,waste | {'pump': 'yes', 'feed_pressure': 85, 'erd': 'no', 'water_type': ['upw_brine']}
upw | nawi | zld_c | treated_storage | treatment | treated_storage | industrial | outlet | {'hours': 24}
upw | nawi | zld_c | holding_tank | intake | holding_tank | media_filtration,media_filtration_2 | outlet,outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['fab25']}
upw | nawi | zld_c | basic_unit | treatment | media_filtration | uv_aop | outlet | {'unit_process_name': 'media_filtration'}
upw | nawi | zld_c | uv_aop | treatment | uv_aop | gac_gravity | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'}
upw | nawi | zld_c | gac_gravity | treatment | gac_gravity | ultra_filtration | outlet | {'ebct': 30}
upw | nawi | zld_c | basic_unit | treatment | ultra_filtration | treated_storage_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | zld_c | treated_storage | treatment | treated_storage_2 | industrial_2 | outlet | {'hours': 24}
upw | nawi | zld_c | basic_unit | treatment | media_filtration_2 | ultra_filtration_2 | outlet | {'unit_process_name': 'media_filtration'}
upw | nawi | zld_c | basic_unit | treatment | ultra_filtration_2 | gac_gravity_2,municipal_wwtp | outlet,waste | {'unit_process_name': 'ultra_filtration'}
upw | nawi | zld_c | gac_gravity | treatment | gac_gravity_2 | ro_first_pass | outlet | {'ebct': 30}
upw | nawi | zld_c | reverse_osmosis | treatment | ro_first_pass | treated_storage_3,passthrough | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
upw | nawi | zld_c | basic_unit | treatment | passthrough | lime_softening | outlet | {'unit_process_name': 'passthrough'}
upw | nawi | zld_c | lime_softening | treatment | lime_softening | ro_second_pass | outlet | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 100}
upw | nawi | zld_c | reverse_osmosis | treatment | ro_second_pass | treated_storage_3,brine_concentrator | outlet,waste | {'feed_pressure': 20, 'erd': 'no', 'pump': 'yes'}
upw | nawi | zld_c | treated_storage | treatment | treated_storage_3 | cooling_supply | outlet | {'hours': 3}
upw | nawi | zld_c | brine_concentrator | treatment | brine_concentrator | crystallizer | outlet
upw | nawi | zld_c | crystallizer | treatment | crystallizer | landfill_zld | waste | {'approach': 'wt3'}
upw | nawi | zld_c | basic_unit | use | cooling_supply |  |  | {'unit_process_name': 'cooling_supply'}
upw | nawi | zld_c | basic_unit | use | industrial |  |  | {'unit_process_name': 'industrial'}
upw | nawi | zld_c | basic_unit | use | industrial_2 |  |  | {'unit_process_name': 'industrial'}
upw | nawi | zld_c | basic_unit | waste | municipal_wwtp |  |  | {'unit_process_name': 'municipal_wwtp'}
upw | nawi | zld_c | landfill_zld | waste | landfill_zld |  |  | {'pipe_distance': 0, 'lift_height': 400}
Conventional
kern_county | nawi | baseline | basic_unit | intake | primary_separator | sedimentation | outlet | {'unit_process_name': 'primary_separator', 'water_type': ['produced_water']}
kern_county | nawi | baseline | sedimentation | treatment | sedimentation | air_flotation | outlet | {'settling_velocity': 0.005}
kern_county | nawi | baseline | basic_unit | treatment | air_flotation | walnut_shell_filter | outlet | {'unit_process_name': 'air_flotation'}
kern_county | nawi | baseline | basic_unit | treatment | walnut_shell_filter | blending_reservoir,landfill | outlet,waste | {'unit_process_name': 'walnut_shell_filter'}
kern_county | nawi | baseline | basic_unit | intake | blending_reservoir | irrigation | outlet | {'unit_process_name': 'blending_reservoir', 'water_type': ['surface_water']}
kern_county | nawi | baseline | basic_unit | use | irrigation |  |  | {'unit_process_name': 'irrigation'}
kern_county | nawi | baseline | landfill | waste | landfill
what-if: higher TDS (30-40 g/L) and Boron: adding electro dialysis, pH adjustment, and RO after walnut shell filter to compensate. Goal of 450 TDS at output
kern_county | nawi | edr_ph_ro | basic_unit | intake | primary_separator | sedimentation | outlet | {'unit_process_name': 'primary_separator', 'water_type': ['produced_water']}
kern_county | nawi | edr_ph_ro | sedimentation | treatment | sedimentation | air_flotation | outlet | {'settling_velocity': 0.005}
kern_county | nawi | edr_ph_ro | basic_unit | treatment | air_flotation | walnut_shell_filter | outlet | {'unit_process_name': 'air_flotation'}
kern_county | nawi | edr_ph_ro | basic_unit | treatment | walnut_shell_filter | electrodialysis_reversal,injection_well_disposal | outlet,waste | {'unit_process_name': 'walnut_shell_filter'}
kern_county | nawi | edr_ph_ro | basic_unit | treatment | electrodialysis_reversal | ph_adjustment,injection_well_disposal | outlet,waste | {'unit_process_name': 'electrodialysis_reversal'}
kern_county | nawi | edr_ph_ro | basic_unit | treatment | ph_adjustment | reverse_osmosis | outlet | {'unit_process_name': 'passthrough'}
kern_county | nawi | edr_ph_ro | reverse_osmosis | treatment | reverse_osmosis | blending_reservoir,injection_well_disposal | outlet,waste | {'pump': 'yes', 'feed_pressure': 65, 'erd': 'no'}
kern_county | nawi | edr_ph_ro | basic_unit | intake | blending_reservoir | irrigation | outlet | {'unit_process_name': 'blending_reservoir', 'water_type': ['surface_water']}
kern_county | nawi | edr_ph_ro | basic_unit | use | irrigation |  |  | {'unit_process_name': 'irrigation'}
kern_county | nawi | edr_ph_ro | basic_unit | waste | injection_well_disposal |  |  | {'unit_process_name': 'injection_well_disposal'}
what-if: higher TDS (30-40 g/L), adding microfiltration and RO to compensate. Goal of 450 TDS at output
kern_county | nawi | ro_and_mf | basic_unit | intake | primary_separator | sedimentation | outlet | {'unit_process_name': 'primary_separator', 'water_type': ['produced_water']}
kern_county | nawi | ro_and_mf | sedimentation | treatment | sedimentation | air_flotation | outlet | {'settling_velocity': 0.005}
kern_county | nawi | ro_and_mf | basic_unit | treatment | air_flotation | walnut_shell_filter | outlet | {'unit_process_name': 'air_flotation'}
kern_county | nawi | ro_and_mf | basic_unit | treatment | walnut_shell_filter | microfiltration,injection_well_disposal | outlet,waste | {'unit_process_name': 'walnut_shell_filter'}
kern_county | nawi | ro_and_mf | microfiltration | treatment | microfiltration | reverse_osmosis,injection_well_disposal | outlet,waste
kern_county | nawi | ro_and_mf | reverse_osmosis | treatment | reverse_osmosis | blending_reservoir,injection_well_disposal | outlet,waste | {'pump': 'yes', 'feed_pressure': 65, 'erd': 'no'}
kern_county | nawi | ro_and_mf | basic_unit | intake | blending_reservoir | irrigation | outlet | {'unit_process_name': 'blending_reservoir', 'water_type': ['surface_water']}
kern_county | nawi | ro_and_mf | basic_unit | use | irrigation |  |  | {'unit_process_name': 'irrigation'}
kern_county | nawi | ro_and_mf | basic_unit | waste | injection_well_disposal |  |  | {'unit_process_name': 'injection_well_disposal'}
damodar | nawi | baseline | holding_tank | intake | holding_tank | microfiltration | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['powder_river_basin_cbm']}
damodar | nawi | baseline | microfiltration | treatment | microfiltration | reverse_osmosis,waiv | outlet,waste
damodar | nawi | baseline | reverse_osmosis | treatment | reverse_osmosis | uv_aop,waiv | outlet,waste | {'pump': 'yes', 'type':'pass', 'feed_pressure': 85, 'erd': 'no'}
damodar | nawi | baseline | uv_aop | treatment | uv_aop | chlorination | outlet | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'}
damodar | nawi | baseline | chlorination | treatment | chlorination | municipal_drinking | outlet | {'chemical_name': 'Chlorine'}
damodar | nawi | baseline | municipal_drinking | use | municipal_drinking
damodar | nawi | baseline | basic_unit | waste | waiv |  |  | {'unit_process_name': 'waiv'}
produced_water_injection | nawi | baseline | basic_unit | intake | passthrough | injection_well_disposal | outlet | {'unit_process_name': 'passthrough', 'water_type': ['produced_water_for_dw']}
produced_water_injection | nawi | baseline | basic_unit | use | injection_well_disposal |  |  | {'unit_process_name': 'injection_well_disposal'}
what if: Brine intensification technology to reduce the brine (MVR Distillation = brine concentrator)
produced_water_injection | nawi | swd_well | holding_tank | intake | holding_tank | coag_and_floc | outlet | {'avg_storage_time': 24, 'surge_cap': 0.2, 'water_type': ['produced_water_for_dw']}
produced_water_injection | nawi | swd_well | coag_and_floc | treatment | coag_and_floc | sedimentation,solids_dewatering_disposal | outlet,waste | {'alum_dose' : 10, 'polymer_dose': 0.1}
produced_water_injection | nawi | swd_well | sedimentation | treatment | sedimentation | ph_adjustment,solids_dewatering_disposal | outlet,waste | {'settling_velocity': 0.005}
produced_water_injection | nawi | swd_well | basic_unit | treatment | ph_adjustment | brine_concentrator | outlet | {'unit_process_name': 'passthrough'}
produced_water_injection | nawi | swd_well | brine_concentrator | treatment | brine_concentrator | injection_well_disposal | outlet
produced_water_injection | nawi | swd_well | basic_unit | use | injection_well_disposal |  |  | {'unit_process_name': 'injection_well_disposal'}
produced_water_injection | nawi | swd_well | basic_unit | waste | solids_dewatering_disposal |  |  | {'unit_process_name': 'injection_well_disposal'}
Note on C561: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: With disposal costs
Note on C569: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Without disposal costs
Note on F632: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No cost for distribution

## parameters
unit process | parameter dictionary | units | notes
ANY THAT HAS A SPLIT STREAM OUT - EXAMPLE IN PARAM DICT IS FOR 3 WAY SPLIT | {'split_faction': [X, X, X]} | fraction of flow to each unit | If the stream is split, specify the proporation of flow that goes to each outlet. The number of outlets must match length of split list.
cooling_tower | See Word Document for cooling tower | See Word Document for cooling tower | See Word Document for cooling tower
ro_deep | {'cost_type': 'first' or 'second', 'feed_pressure': value, 'type': 'pass' or 'stage', 'erd': 'yes' or 'no'} | feed_pressure = bar | ERD Setting is important and user can input wrong value if not careful
reverse_osmosis | {'feed_pressure': value, 'membrane_area': value, 'type': 'pass' or 'stage', 'erd': 'yes' or 'no'} | feed_pressure = bar, membrane_area = m2 | ERD Setting is important and user can input wrong value if not careful
ammonia_addition | {'chemical_name': ['Ammonia'], 'dose': 3} | dose = mg/L
anion_exchange | {'tds_in': 15} | tds_in = mg/L | tds_in is sulfate concentration into IX.
anti_scalant_addition | {'chemical_name': ['Hydrazine_(N2H4)'], 'dose': 5} | dose = mg/L
backwash_solids_handling | {'recovery': 0.95} | recovert = fraction from 0-1
cation_exchange | {'tds_in': 100} | tds_in = mg/L
caustic_soda_addition | {'chemical_name': ['Sodium_Hydroxide_(NaOH)'], 'dose': 3} | dose = mg/L
chlorination | {'chemical_name': ['Chlorine']} |  | other forms of chlorine available
coag_and_floc | {'alum_dose' : 10, 'polymer_dose': 0.1} | alum_dose = mg/L, polymer_dose = mg/L
coagulant_addition | {'chemical_name': ['Iron_FeCl3'], 'dose': 0.03} | dose = mg/L
deep_well_injection | {'incl_piping': True, 'pipe_distance': 22} | pipe_distance = miles | If incl_piping is True, 22 miles of piping is included by default. Otherwise user can specify the miles of piping.
evaporation_pond | {'approach': 'wt3' or 'zld', 'evap_method': 'jensen' or 'turc', 'air_temp': 30, 'solar_rad': 25} | air_temp = Celsius, solar_rad = mJ/m2 | ZLD shouldn't be used unless evaporation pond is after brine concentrator. Recommend using WT3 approach for now.
ferric_chloride_addition | {'chemical_name': ['Iron_FeCl3'], 'dose': 20} | dose = mg/L
gac_gravity | {'ebct': 12} | ebct = minutes
gac_pressure_vessel | {'ebct': 12} | ebct = minutes
holding_tank | {'avg_storage_time': 1, 'surge_cap': 0.2} | avg_storage_time = hours, surge_cap = % of avg_storage_tme
hydrochloric_acid_addition | {'chemical_name': ['Hydrochloric_Acid_(HCl)'], 'dose': 0.01} | dose = mg/L
lime_softening | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3} | dose = mg/L
lime_addition | {'chemical_name': ['Lime_Suspension_CaOH_2'], 'lime': 2.3} | dose = mg/L
ozone_aop | {'chemical_name': ['Hydrogen_Peroxide'], 'contact_time': 1, 'ct': 1, 'mass_transfer': 0.8, 'aop': False} | contact_time = minutes, ct = minutes, mass_transfer = dimensionless
packed_tower_aeration | {'radon_rem': 0.88} | radon_rem = dimensionless
sedimentation | {'settling_velocity': 0.005} | settling_velocity = m/s | Could add more basin design customization
sodium_bisulfite_addition | {'chemical_name': ['Sodium_Bisullfite_NaHSO3'], 'dose': 0.01} | dose = mg/L
sulfuric_acid_addition | {'chemical_name': ['Sulphuric_Acid_H2SO4'], 'dose': 0.01} | dose = mg/L
treated_storage | {'hours': 24} | hours = hours
uv_aop | {'chemical_name': ['Hydrogen_Peroxide'], 'dose': 5, 'uv_dose': 80, 'aop': 'True'} | uv_dose = mJ/cm2, dose = mg/L | "dose" is H2O2 dose used if AOP
water_pumping_station | {'pump_type': 'raw', 'tdh': 50} | pump_type is either 'raw' or 'treated', tdh = feet | tdh is a necessary input but is not currently used in cost calculation but will be incorporated in a future version.
basic_unit | {'unit_process_name': 'unit_process'} |  | Basic unit is a cost curve as a function of flow.
unit_process' can be any of the following:
abmet_intermediate_pump
abmet_interstage_pump
aeration_basin1
aeration_basin2
aeration_tank
agriculture
air_flotation
anaerobic_digestion_oxidation
anti_oxidant_addition
bio_active_filtration
bioreactor
bioreactor_bw_pump
bioreactor_effluent_pump
bioreactor_feed_pump
blending_reservoir
brine_concentrator_crystallizer
brine_ro
buffer_tank
cas
cas_denitrif
cas_nitrif
chlorination
clarifier
coagulant_addition
coal_plant_cooling_tower
cooling_supply
crystallizer_waterreuse
decarbonator
decarbonator_a
decarbonator_b
decarbonator_waterreuse
deep_bed_filtration
deep_well
deep_well_injection
direct_injection
discharge
disinfection
dissolved_air_flotation
drainage_sump_pump1
drainage_sump_pump2
dual_media_filtration
electro_deionization
electrodialysis_reversal
engineered_buffer_with_chloramine
engineered_buffer_with_chlorine
evaporation_pond_waterreuse
fc_crystallizer
feed_water_tank
gac_feed_pump
industrial
injection_well_disposal
injection_well_treat
injection_well_use
intrusion_mitigation
irrigation
irwin_brackish
irwin_brine
irwin_brine_management
mbr_denitrification
mbr_nitrification
media_filtration
microfiltration
microscreen_filtration
mining
municipal_wwtp
nano_filtration
oil_and_gas
onsite_storage
primary_separator
pumping_station
raw_water_pump1
raw_water_pump2
recharge_pump_well
screen
settling_pond
silica_solution
sludge_tank
smp
soil_aquifer_treatment
static_mixer
sulfuric_acid_addition
surface_augmentation
tramp_oil_tank
tuscarora_md
uf_feed_pump
ultra_filtration
waiv
walnut_shell_filter